## Front
SUBMITTAL DATA
B Series Multi-Position & Hydronic Air Handlers
Job: |  |  |  | Engineer:
Location: |  |  |  | Architect:
Schedule No.: |  |  |  | Date:
System Designation: |  |  |  | For:
FEATURES
Product Warranty
Optional Accessories
Unit Size
|  | BCRM00124S003R | BVRM00125S003R | BCRM00124S001R | BVRM00125S001R
Heat Options |  | No heat | No heat | No heat | No heat
Refrigerant |  | R-454B | R-454B | R-454B | R-454B
Factory Installed metering device |  | Piston | Piston | Piston | Piston
Blower Data: | Motor Type | 3-speed PSC motor | Variable speed high eff. ECM motor | 3-speed PSC motor | Variable speed high eff. ECM motor
| Motor H.P. | 1/3 | 1/3 | 1/3 | 1/3
| F.L.A. | 3.2 | 4.8 | 1.8 | 2.4
Cooling CFM |  | 800 | 600 - 1000 | 800 | 600 - 1000
Heating CFM |  | 800 | 600 - 1000 | 800 | 600 - 1000
Max Unit Weight (lbs) |  | 120 | 130 | 120 | 130
Available Voltages |  | 120 V, 60 Hz, 1 Ph | 120 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph
Transformer Size and Type |  | 40 VA, Class 2 | 40 VA, Class 2 | 40 VA, Class 2 | 40 VA, Class 2
Refrigerant Conn. (IDS) Suction |  | 3/4 | 3/4 | 3/4 | 3/4
Refrigerant Conn. (IDS) Liquid |  | 3/8 | 3/8 | 3/8 | 3/8
Min order qty |  | 4 | 4 | 4 | 4
NOTES:
Cooling capacities subject to outdoor unit matchup. See http://www.adpnow.com/extratings/ for individual capacities by OEM
Cooling and Heating capacity data is rated at the following conditions:
Cooling: 80 FDB / 67 FWB Indoor, 95 FDB Outdoor
Heating: 70 FDB / 47 FWB Indoor, 43 FDB Outdoor
| A1 Refrigerants Product Nomenclature |  |  | A2L Refrigerants Product Nomenclature
2140 Lake Park Blvd., Richardson, TX 75080
www.adpnow.com
Multi-position available from factory, or field convertible with accessory kit.
Coils are air pressure tested at 500psi, leak tested with helium, sealed with rubber plugs, and then charged with dry air.
Easy to adjust blower speeds for fine tuning customer comfort.
Dynamically balanced blowers for quiet, vibration-free operation.
Microban® antimicrobial additive to inhibit the growth of mold and mildew in the drain pan.
A1 model Suitable for use with R-22 and R-410A.
A2L model Suitable for use with R-32 and R-454B.
A2L model include factory installed Refrigerant Detections System (RDS).
Hot water heat kits available both factory and field installed.
Variable-Speed High Efficiency ECM Motor available.
Piston or HP-A/C TXV available factory installed. Screw-on TXVs available as kits for field installation
5-year limited warranty (Terms & Conditions Apply).
Product improvement is a continuous process at Advanced Distributor Products. Therefore, product specifications are subject to change without notice and without obligation on our part. Please contact your ADP representative or distributor to verify details.
© 2025 by Advanced Distributor Products. All rights reserved.

## Back
SUBMITTAL DATA
B Series Multi-Position & Hydronic Air Handlers
Dimensions | [10 empty] | Supply Duct Opening |  |  |  | Return Duct Opening
Air Handler Size | [5 empty] | A (in) |  |  | B (in) | C (in) | Depth (in) |  | Width (in) |  | Depth (in) |  | Width (in)
BCRM00124S003R | [5 empty] | 44 |  |  | 22 | 15 | 17 |  | 13.5 |  | 20 |  | 12.5
BVRM00125S003R | [5 empty] | 48 |  |  | 22 | 18.5 | 17 |  | 17 |  | 20 |  | 16
BCRM00124S001R | [5 empty] | 44 |  |  | 22 | 15 | 17 |  | 13.5 |  | 20 |  | 12.5
BVRM00125S001R | [5 empty] | 48 |  |  | 22 | 18.5 | 17 |  | 17 |  | 20 |  | 16
| Airflow (CFM) vs. External Static Pressure (inches W.C.) | [8 empty] | Electric Data
Unit Size | Fan Speed Setting | 0.1 | 0.2 | 0.3 | 0.4 | 0.5
BCRM00124S003R | Low | 687 | 584 | 579 | 549 | 487
| Med | 889 | 847 | 795 | 731 | 666
| *High | 952 | 896 | 847 | 780 | 697
|  | Cool |  |  |  | Heat
Unit Size | Operating Mode | A | B | C | D | A | B | C | D
BVRM00125S003R | Continuous Blower | Cool A: 500; Cool B: 400; Cool C: 350; Cool D: 350
| Hi Cooling / HP Heating | Cool A: 1000; Cool B: 800; Cool C: 700; Cool D: 600 | Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Total Current, (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size per stage (A)
| Low Cooling / HP Heating | Cool A: 700; Cool B: 560; Cool C: 490; Cool D: 420 |  |  |  | kW | BTUH
| Aux. Heat | *** | *** | *** | *** | 1000 | 800 | 700* | 600* |  |  |  | 240 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| Emer. Heat | *** | *** | *** | *** | 1000 | 800 | 700* | 600* | BCRM00124S001R | CKT 1 | 0 | 0 | 0 | 1.9 | 1.8 | 1.9 | 1.8 | 2.375 | 2.25 | 15 | 15
[10 empty] | Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Total Current, (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size per stage (A)
Unit Size | Fan Speed Setting | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | [6 empty] | kW | BTUH
BCRM00124S001R | Low | 640 | 635 | 619 | 584 | 513 | [6 empty] | 240 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| Med | 907 | 861 | 808 | 743 | 659 |  |  |  | BVRM00125S001R | CKT 1 | 0 | 0 | 0 | 2.6 | 2.4 | 2.6 | 2.4 | 3.25 | 3 | 15 | 15
| *High | 961 | 914 | 854 | 786 | 703
[10 empty] | Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Total Current, (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size per stage (A)
[13 empty] | kW | BTUH
|  | Cool A: Cool; Heat A: Heat |  |  |  | 120 V | 120 V | 120 V |  | 120 V |  | 120 V |  | 120 V
Unit Size | Operating Mode | A | B | C | D | A | B | C | D | BCRM00124S003R | CKT 1 | 0 | 0 | 0 | 3.2 |  | 3.2 |  | 4 |  | 15
BVRM00125S001R | Continuous Blower | Cool A: 500; Cool B: 400; Cool C: 350; Cool D: 350
| Hi Cooling / HP Heating | Cool A: 1000; Cool B: 800; Cool C: 700; Cool D: 600 | Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Total Current, (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size per stage (A)
| Low Cooling / HP Heating | Cool A: 700; Cool B: 560; Cool C: 490; Cool D: 420 |  |  |  | kW | BTUH
| Aux. Heat | *** | *** | *** | *** | 1000 | 800 | 700* | 600* |  |  |  | 120 V | 120 V | 120 V |  | 120 V |  | 120 V |  | 120 V
| Emer. Heat | *** | *** | *** | *** | 1000 | 800 | 700* | 600* | BVRM00125S003R | CKT 1 | 0 | 0 | 0 | 4.8 |  | 4.8 |  | 6 |  | 15
Speeds marked with asterisk** are the factory speed settings for both heating and cooling.
* This CFM is not approved for use with the highest kW heater size.
***Airflow is the greater of the COOL and HEAT values when both electric heat and heat pump
are operating.

## Nomenclature (hidden)
B | C |  | R |  | M |  | A3 | 9 |  | 24 | S | 3P |  | 3 |  | A
Series | Blower Motor |  | Horizontal Drain Pan Position |  | Airflow Config. |  | Slab No. | Metering Device |  | Unit Size | Line Voltage Connection | Heat Options |  | Voltage |  | Revision | Revision
B | C: | 3-speed PSC motor | R: | Right-hand | M: | Multi-pos. |  | 0: | No cooling coil | 12 18 24 25 30 31 36 37 42 48 60 | S = Stripped wire | 00: | No heat | 1: | 208/240 V, 60 Hz, 1 ph.
| V: | Variable-speed high eff. ECM motor | O: | No cooling coil |  |  |  | 1: | Piston (R-410A) |  |  | Hot Water Coil w/ Pump & Valve Assembly |  | 3: | 120 V, 60 Hz, 1 ph.
[8 empty] | 7: | Bleed HP-A/C TXV (R-410A) |  |  | 2P: | 2 row hot water coil [sizes 12-30,36] | 4: | 120 V, 60 Hz, 1 ph. & 130̊ F aquastat
[8 empty] | 9: | Non-bleed HP-A/C TXV (R-410A) |  |  | 3P: | 3 row hot water coil [all sizes]
[12 empty] | 4P: | 4 row hot water coil [sizes 31,37-60]
Hot Water Coil w/o Pump & Valve Assembly
[12 empty] | 2N: | 2 row hot water coil [sizes 12-30,36]
[12 empty] | 3N: | 3 row hot water coil [all sizes]
[12 empty] | 4N: | 4 row hot water coil [sizes 31,37-60]
B | C |  | R |  | M |  | A3 | A: |  | 24 | S | 3P |  | 3 |  | R
Series | Blower Motor |  | Horizontal Drain Pan Position |  | Airflow Config. |  | Slab No. | Metering Device |  | Unit Size | Line Voltage Connection | Heat Options |  | Voltage |  | Refrigerant Detection System
B | C: | 3-speed PSC motor | R: | Right-hand | M: | Multi-pos. |  | 1: | Piston (R-454B & R-32) | 12 18 24 25 30 31 36 37 42 48 60 | S = Stripped wire | 00: | No heat | 1: | 208/240 V, 60 Hz, 1 ph. | R: | Included (Factory installed)
| V: | Variable-speed high eff. ECM motor | O: | No cooling coil |  |  |  | A: | Non-bleed HP-A/C TXV (R-454B) |  |  | Hot Water Coil w/ Pump & Valve Assembly |  | 3: | 120 V, 60 Hz, 1 ph.
[8 empty] | B: | Non-bleed HP-A/C TXV (R-32) |  |  | 2P: | 2 row hot water coil [sizes 12-30,36] | 4: | 120 V, 60 Hz, 1 ph. & 130̊ F aquastat
[8 empty] | C: | Bleed HP-A/C TXV (R-454B) |  |  | 3P: | 3 row hot water coil [all sizes]
[12 empty] | 4P: | 4 row hot water coil [sizes 31,37-60]
Hot Water Coil w/o Pump & Valve Assembly
[12 empty] | 2N: | 2 row hot water coil [sizes 12-30,36]
[12 empty] | 3N: | 3 row hot water coil [all sizes]
[12 empty] | 4N: | 4 row hot water coil [sizes 31,37-60]

## Data (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
Part Number | Series | Blower Motor | Airflow Config. | Slab No. | Metering Device | Unit Size | Line Voltage Connection | Electric Heat | Voltage | Revision | Refrigerant (R22 or R-410A) | Factory Installed metering device | Blower Data: Motor H.P. | Blower Data: F.L.A. @ 240 V | Nominal CFM | Max Unit Weight (lbs) | Available Voltages | Maximum Elec. Heat available (kW) | Transformer Size and Type | Refrigerant Conn. (IDS) Suction | Refrigerant Conn. (IDS) Liquid | Pallet Quantity (min order per model) | Horizontal Drain Pan Position | Cooling CFM | Heating CFM | Heat option
BCRM00124S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00124S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00124S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00125S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00125S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00125S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00136S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00136S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00136S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00136S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00136S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00136S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00136S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00136S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00136S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00136S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00136S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00137S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00137S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00137S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00148S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00148S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00148S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00160S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00160S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00160S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00A24S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00A24S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00A24S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A25S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00A25S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00A25S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00A36S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00A36S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00A36S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00A36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A37S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00A37S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00A37S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00A48S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00A48S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00A48S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00A60S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00A60S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00A60S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00B24S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00B24S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00B24S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B25S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00B25S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00B25S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00B36S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00B36S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00B36S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00B36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B37S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00B37S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00B37S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00B48S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00B48S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00B48S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00B60S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00B60S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00B60S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00C24S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00C24S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00C24S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C25S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00C25S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00C25S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRM00C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRM00C36S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00C36S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00C36S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00C36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C37S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00C37S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00C37S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRM00C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRM00C48S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00C48S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00C48S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRM00C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRM00C60S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00C60S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00C60S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRM00C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRM00C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMA1112S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1112S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1112S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1118S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1118S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1118S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1124S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1124S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1124S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA1C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA1C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA1C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA1C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA1C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA1C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2112S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2112S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2112S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2118S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2118S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2118S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2124S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2124S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2124S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA2C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA2C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA2C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA2C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA2C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA2C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3112S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3112S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3112S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3118S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3118S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3118S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3124S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3124S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3124S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA3C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA3C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA3C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA3C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA3C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA3C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4112S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4112S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4112S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4118S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4118S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4118S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4124S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4124S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4124S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA4C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA4C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA4C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA4C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA4C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA4C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6112S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6112S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6112S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6118S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6118S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6118S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6124S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6124S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6124S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA6C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA6C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA6C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA6C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA6C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA6C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7112S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7112S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7112S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7118S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7118S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7118S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7124S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7124S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7124S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA7C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA7C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA7C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA7C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA7C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA7C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8112S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8112S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8112S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8118S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8118S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8118S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8124S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8124S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8124S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | No heat
BCRMA8C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 400 | 400 | Hot water Coil
BCRMA8C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | No heat
BCRMA8C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 | 600 | Hot water Coil
BCRMA8C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA8C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA8C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9125S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9125S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9125S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9130S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9130S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9130S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9A25S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9A25S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9A25S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9A30S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9A30S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9A30S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9B25S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9B25S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9B25S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9B30S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9B30S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9B30S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9C25S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9C25S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9C25S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMA9C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMA9C30S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9C30S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9C30S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMA9C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMA9C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1125S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1125S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1125S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1130S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1130S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1130S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB1C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB1C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB1C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB1C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2125S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2125S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2125S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2130S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2130S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2130S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB2C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB2C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB2C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB2C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB3125S001R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3125S003R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3125S004R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB3C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB3C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4125S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4125S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4125S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4130S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4130S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4130S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4136S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4136S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4136S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4136S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4136S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4136S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4136S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4136S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4136S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4136S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4136S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4A36S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4A36S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4A36S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4A36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4A36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4A36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4A36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4A36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4A36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4A36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4A36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4B36S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4B36S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4B36S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4B36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4B36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4B36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4B36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4B36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4B36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4B36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4B36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB4C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB4C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB4C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB4C36S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4C36S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4C36S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB4C36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4C36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4C36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4C36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4C36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4C36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4C36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB4C36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5125S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5125S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5125S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5130S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5130S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5130S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5136S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5136S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5136S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5136S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5136S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5136S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5136S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5136S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5136S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5136S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5136S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5A36S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5A36S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5A36S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5A36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5A36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5A36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5A36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5A36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5A36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5A36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5A36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5B36S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5B36S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5B36S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5B36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5B36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5B36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5B36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5B36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5B36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5B36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5B36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB5C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB5C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB5C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB5C36S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5C36S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5C36S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB5C36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5C36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5C36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5C36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5C36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5C36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5C36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB5C36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6125S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6125S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6125S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6130S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6130S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6130S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6136S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6136S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6136S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6136S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6136S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6136S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6136S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6136S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6136S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6136S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6136S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6A36S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6A36S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6A36S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6A36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6A36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6A36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6A36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6A36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6A36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6A36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6A36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6B36S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6B36S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6B36S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6B36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6B36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6B36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6B36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6B36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6B36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6B36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6B36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB6C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB6C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB6C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB6C36S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6C36S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6C36S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB6C36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6C36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6C36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6C36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6C36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6C36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6C36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB6C36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7125S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7125S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7125S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7130S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7130S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7130S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7136S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7136S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7136S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7136S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7136S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7136S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7136S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7136S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7136S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7136S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7136S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7A36S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7A36S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7A36S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7A36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7A36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7A36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7A36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7A36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7A36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7A36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7A36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7B36S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7B36S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7B36S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7B36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7B36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7B36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7B36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7B36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7B36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7B36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7B36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | No heat
BCRMB7C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 800 | 800 | Hot water Coil
BCRMB7C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB7C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB7C36S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7C36S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7C36S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB7C36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7C36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7C36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7C36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7C36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7C36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7C36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB7C36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8137S001R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8137S003R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8137S004R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8A37S001R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8A37S003R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8A37S004R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8B37S001R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8B37S003R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8B37S004R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8C37S001R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8C37S003R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8C37S004R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB8C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB8C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9131S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9131S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9131S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9137S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9137S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9137S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9142S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9142S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9142S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9148S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9148S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9148S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9A31S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9A31S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9A31S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9A37S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9A37S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9A37S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9A42S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9A42S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9A42S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9A48S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9A48S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9A48S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9B31S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9B31S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9B31S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9B37S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9B37S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9B37S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9B42S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9B42S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9B42S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9B48S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9B48S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9B48S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9C31S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9C31S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9C31S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMB9C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMB9C37S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9C37S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9C37S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMB9C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMB9C42S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9C42S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9C42S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMB9C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMB9C48S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9C48S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9C48S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMB9C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMB9C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1131S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1131S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1131S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1137S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1137S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1137S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1142S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1142S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1142S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1148S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1148S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1148S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC1C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC1C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC1C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC1C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC1C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC1C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC1C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC1C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3131S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3131S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3131S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3137S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3137S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3137S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3142S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3142S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3142S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3148S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3148S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3148S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3160S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3160S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3160S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC3C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC3C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC3C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC3C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC3C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC3C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC3C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC3C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC3C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC3C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4131S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4131S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4131S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4137S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4137S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4137S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4142S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4142S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4142S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4148S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4148S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4148S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4160S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4160S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4160S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC4C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC4C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC4C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC4C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC4C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC4C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC4C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC4C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC4C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC4C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5131S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5131S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5131S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5137S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5137S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5137S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5142S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5142S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5142S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5148S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5148S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5148S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5160S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5160S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5160S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC5C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC5C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC5C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC5C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC5C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC5C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC5C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC5C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC5C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC5C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6131S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6131S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6131S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6137S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6137S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6137S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6142S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6142S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6142S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6148S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6148S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6148S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6160S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6160S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6160S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC6C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC6C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC6C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC6C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC6C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC6C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC6C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC6C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC6C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC6C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7131S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7131S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7131S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7137S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7137S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7137S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7142S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7142S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7142S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7148S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7148S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7148S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7160S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7160S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7160S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | No heat
BCRMC7C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 | 1000 | Hot water Coil
BCRMC7C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | No heat
BCRMC7C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 | 1200 | Hot water Coil
BCRMC7C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | No heat
BCRMC7C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1400 | 1400 | Hot water Coil
BCRMC7C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | No heat
BCRMC7C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1600 | 1600 | Hot water Coil
BCRMC7C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC7C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC7C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9160S001R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9160S003R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9160S004R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMC9C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMC9C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1160S001R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1160S003R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1160S004R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1A60S001R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1A60S003R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1A60S004R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1B60S001R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1B60S003R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1B60S004R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1C60S001R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1C60S003R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1C60S004R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | No heat
BCRMD1C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCRMD1C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 2000 | 2000 | Hot water Coil
BCOM00124S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00124S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00124S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00125S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00125S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00125S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00136S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00136S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00136S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00136S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00136S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00136S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00136S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00136S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00136S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00136S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00136S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00137S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00137S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00137S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00148S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00148S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00148S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00160S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00160S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00160S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00A24S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00A24S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00A24S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A25S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00A25S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00A25S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00A36S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00A36S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00A36S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00A36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A37S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00A37S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00A37S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00A48S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00A48S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00A48S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00A60S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00A60S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00A60S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00B24S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00B24S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00B24S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B25S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00B25S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00B25S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00B36S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00B36S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00B36S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00B36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B37S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00B37S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00B37S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00B48S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00B48S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00B48S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00B60S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00B60S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00B60S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00C24S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00C24S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00C24S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C25S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00C25S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00C25S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOM00C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOM00C36S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00C36S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00C36S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00C36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C37S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00C37S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00C37S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOM00C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOM00C48S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00C48S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00C48S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOM00C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOM00C60S001R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00C60S003R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00C60S004R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOM00C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOM00C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMA1112S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1112S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1112S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1118S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1118S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1118S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1124S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1124S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1124S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA1C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA1C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA1C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA1C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA1C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA1C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A1 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2112S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2112S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2112S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2118S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2118S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2118S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2124S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2124S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2124S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA2C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA2C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA2C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA2C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA2C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA2C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A2 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3112S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3112S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3112S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3118S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3118S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3118S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3124S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3124S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3124S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA3C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA3C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA3C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA3C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA3C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA3C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A3 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4112S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4112S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4112S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4118S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4118S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4118S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4124S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4124S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4124S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA4C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA4C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA4C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA4C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA4C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA4C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A4 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6112S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6112S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6112S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6118S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6118S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6118S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6124S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6124S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6124S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA6C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA6C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA6C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA6C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA6C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA6C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A6 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7112S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7112S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7112S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7118S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7118S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7118S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7124S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7124S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7124S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA7C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA7C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA7C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA7C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA7C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA7C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A7 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8112S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8112S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8112S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8112S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8112S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8112S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8112S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8112S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8112S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8112S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8112S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8118S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8118S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8118S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8118S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8118S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8118S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8118S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8118S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8118S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8118S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8118S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8124S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8124S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8124S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8124S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8124S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8124S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8124S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8124S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8124S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8124S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8124S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Piston (R-454B & R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8A12S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8A12S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8A12S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8A12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8A12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8A12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8A12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8A12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8A12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8A12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8A12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8A18S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8A18S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8A18S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8A18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8A18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8A18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8A18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8A18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8A18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8A18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8A18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8A24S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8A24S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8A24S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8A24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8A24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8A24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8A24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8A24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8A24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8A24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8A24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8B12S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8B12S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8B12S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8B12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8B12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8B12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8B12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8B12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8B12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8B12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8B12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8B18S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8B18S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8B18S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8B18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8B18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8B18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8B18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8B18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8B18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8B18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8B18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8B24S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8B24S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8B24S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8B24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8B24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8B24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8B24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8B24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8B24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8B24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8B24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8C12S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8C12S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8C12S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | No heat
BCOMA8C12S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8C12S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8C12S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8C12S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8C12S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8C12S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8C12S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8C12S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 12 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 400 | 400 | Hot water Coil
BCOMA8C18S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8C18S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8C18S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | No heat
BCOMA8C18S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8C18S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8C18S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8C18S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8C18S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8C18S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8C18S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8C18S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 | 600 | Hot water Coil
BCOMA8C24S001R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.8 | Not Applicable | 120 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8C24S003R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8C24S004R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA8C24S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8C24S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8C24S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8C24S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8C24S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8C24S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8C24S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA8C24S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A8 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | Not Applicable | 120 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9125S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9125S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9125S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9130S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9130S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9130S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9A25S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9A25S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9A25S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9A30S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9A30S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9A30S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9B25S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9B25S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9B25S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9B30S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9B30S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9B30S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9C25S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9C25S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9C25S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMA9C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMA9C30S001R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9C30S003R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9C30S004R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMA9C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMA9C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1125S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1125S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1125S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1130S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1130S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1130S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB1C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB1C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB1C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB1C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2125S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2125S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2125S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2130S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2130S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2130S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB2C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB2C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB2C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB2C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB3125S001R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3125S003R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3125S004R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB3C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB3C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4125S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4125S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4125S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4130S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4130S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4130S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4136S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4136S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4136S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4136S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4136S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4136S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4136S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4136S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4136S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4136S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4136S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4A36S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4A36S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4A36S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4A36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4A36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4A36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4A36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4A36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4A36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4A36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4A36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4B36S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4B36S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4B36S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4B36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4B36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4B36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4B36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4B36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4B36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4B36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4B36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB4C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB4C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB4C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB4C36S001R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4C36S003R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4C36S004R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB4C36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4C36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4C36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4C36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4C36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4C36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4C36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB4C36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5125S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5125S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5125S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5130S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5130S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5130S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5136S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5136S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5136S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5136S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5136S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5136S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5136S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5136S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5136S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5136S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5136S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5A36S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5A36S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5A36S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5A36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5A36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5A36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5A36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5A36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5A36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5A36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5A36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5B36S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5B36S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5B36S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5B36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5B36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5B36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5B36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5B36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5B36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5B36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5B36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB5C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB5C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB5C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB5C36S001R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5C36S003R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5C36S004R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB5C36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5C36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5C36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5C36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5C36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5C36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5C36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB5C36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6125S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6125S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6125S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6130S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6130S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6130S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6136S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6136S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6136S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6136S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6136S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6136S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6136S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6136S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6136S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6136S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6136S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6A36S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6A36S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6A36S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6A36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6A36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6A36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6A36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6A36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6A36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6A36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6A36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6B36S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6B36S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6B36S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6B36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6B36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6B36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6B36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6B36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6B36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6B36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6B36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB6C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB6C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB6C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB6C36S001R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6C36S003R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6C36S004R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB6C36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6C36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6C36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6C36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6C36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6C36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6C36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB6C36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7125S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7125S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7125S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7125S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7125S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7125S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7125S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7125S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7125S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7125S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7125S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7130S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7130S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7130S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7130S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7130S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7130S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7130S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7130S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7130S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7130S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7130S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7136S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7136S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7136S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7136S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7136S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7136S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7136S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7136S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7136S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7136S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7136S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7A25S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7A25S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7A25S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7A25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7A25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7A25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7A25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7A25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7A25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7A25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7A25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7A30S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7A30S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7A30S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7A30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7A30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7A30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7A30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7A30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7A30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7A30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7A30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7A36S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7A36S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7A36S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7A36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7A36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7A36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7A36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7A36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7A36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7A36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7A36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7B25S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7B25S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7B25S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7B25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7B25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7B25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7B25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7B25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7B25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7B25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7B25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7B30S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7B30S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7B30S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7B30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7B30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7B30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7B30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7B30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7B30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7B30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7B30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7B36S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7B36S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7B36S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7B36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7B36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7B36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7B36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7B36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7B36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7B36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7B36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7C25S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7C25S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7C25S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | No heat
BCOMB7C25S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7C25S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7C25S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7C25S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7C25S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7C25S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7C25S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7C25S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 800 | 800 | Hot water Coil
BCOMB7C30S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7C30S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7C30S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB7C30S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7C30S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7C30S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7C30S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7C30S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7C30S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7C30S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7C30S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB7C36S001R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7C36S003R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7C36S004R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB7C36S2P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7C36S2P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7C36S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7C36S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7C36S2N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7C36S2N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7C36S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB7C36S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8137S001R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8137S003R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8137S004R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8A37S001R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8A37S003R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8A37S004R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8B37S001R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8B37S003R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8B37S004R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8C37S001R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8C37S003R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8C37S004R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB8C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB8C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9131S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9131S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9131S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9137S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9137S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9137S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9142S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9142S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9142S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9148S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9148S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9148S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9A31S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9A31S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9A31S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9A37S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9A37S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9A37S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9A42S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9A42S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9A42S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9A48S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9A48S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9A48S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9B31S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9B31S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9B31S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9B37S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9B37S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9B37S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9B42S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9B42S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9B42S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9B48S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9B48S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9B48S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9C31S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9C31S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9C31S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMB9C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMB9C37S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9C37S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9C37S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMB9C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMB9C42S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9C42S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9C42S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMB9C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMB9C48S001R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9C48S003R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9C48S004R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMB9C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMB9C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1131S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1131S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1131S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1137S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1137S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1137S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1142S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1142S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1142S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1148S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1148S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1148S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC1C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC1C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC1C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC1C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC1C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC1C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC1C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC1C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3131S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3131S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3131S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3137S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3137S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3137S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3142S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3142S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3142S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3148S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3148S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3148S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3160S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3160S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3160S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC3C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC3C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC3C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC3C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC3C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC3C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC3C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC3C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC3C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC3C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4131S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4131S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4131S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4137S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4137S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4137S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4142S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4142S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4142S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4148S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4148S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4148S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4160S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4160S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4160S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC4C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC4C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC4C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC4C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC4C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC4C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC4C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC4C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC4C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC4C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5131S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5131S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5131S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5137S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5137S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5137S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5142S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5142S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5142S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5148S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5148S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5148S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5160S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5160S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5160S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC5C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC5C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC5C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC5C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC5C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC5C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC5C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC5C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC5C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC5C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6131S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6131S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6131S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6137S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6137S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6137S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6142S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6142S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6142S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6148S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6148S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6148S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6160S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6160S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6160S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC6C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC6C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC6C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC6C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC6C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC6C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC6C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC6C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC6C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC6C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7131S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7131S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7131S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7131S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7131S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7131S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7131S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7131S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7131S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7131S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7131S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7137S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7137S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7137S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7137S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7137S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7137S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7137S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7137S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7137S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7137S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7137S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7142S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7142S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7142S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7142S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7142S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7142S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7142S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7142S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7142S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7142S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7142S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7148S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7148S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7148S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7148S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7148S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7148S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7148S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7148S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7148S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7148S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7148S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7160S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7160S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7160S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7A31S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7A31S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7A31S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7A31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7A31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7A31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7A31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7A31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7A31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7A31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7A31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7A37S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7A37S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7A37S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7A37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7A37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7A37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7A37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7A37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7A37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7A37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7A37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7A42S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7A42S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7A42S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7A42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7A42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7A42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7A42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7A42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7A42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7A42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7A42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7A48S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7A48S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7A48S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7A48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7A48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7A48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7A48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7A48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7A48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7A48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7A48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7B31S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7B31S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7B31S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7B31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7B31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7B31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7B31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7B31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7B31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7B31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7B31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7B37S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7B37S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7B37S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7B37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7B37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7B37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7B37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7B37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7B37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7B37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7B37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7B42S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7B42S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7B42S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7B42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7B42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7B42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7B42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7B42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7B42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7B42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7B42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7B48S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7B48S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7B48S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7B48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7B48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7B48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7B48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7B48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7B48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7B48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7B48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7C31S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7C31S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7C31S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | No heat
BCOMC7C31S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7C31S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7C31S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7C31S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7C31S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7C31S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7C31S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7C31S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 | 1000 | Hot water Coil
BCOMC7C37S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7C37S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7C37S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | No heat
BCOMC7C37S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7C37S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7C37S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7C37S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7C37S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7C37S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7C37S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7C37S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 7.1 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 | 1200 | Hot water Coil
BCOMC7C42S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7C42S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7C42S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | No heat
BCOMC7C42S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7C42S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7C42S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7C42S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7C42S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7C42S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7C42S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7C42S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1400 | 1400 | Hot water Coil
BCOMC7C48S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7C48S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7C48S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | No heat
BCOMC7C48S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7C48S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7C48S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7C48S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7C48S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7C48S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7C48S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7C48S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1600 | 1600 | Hot water Coil
BCOMC7C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC7C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC7C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9160S001R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9160S003R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9160S004R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9A60S001R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9A60S003R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9A60S004R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9B60S001R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9B60S003R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9B60S004R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9C60S001R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9C60S003R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9C60S004R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMC9C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMC9C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1160S001R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1160S003R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1160S004R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1160S3P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1160S3P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1160S4P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1160S4P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1160S3N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1160S3N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1160S4N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1160S4N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1A60S001R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1A60S003R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1A60S004R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1A60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1A60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1A60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1A60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1A60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1A60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1A60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1A60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1B60S001R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1B60S003R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1B60S004R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1B60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1B60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1B60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1B60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1B60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1B60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1B60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1B60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1C60S001R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1C60S003R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1C60S004R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | No heat
BCOMD1C60S3P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1C60S3P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1C60S4P3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1C60S4P4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1C60S3N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1C60S3N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1C60S4N3R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BCOMD1C60S4N4R | B Series | 3-speed PSC motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 2000 | 2000 | Hot water Coil
BVRM00125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00137S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00137S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00137S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00137S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00137S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00137S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00137S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00137S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00137S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00137S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00137S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00148S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00148S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00148S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00148S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00148S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00148S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00148S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00148S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00148S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00148S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00148S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00160S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00160S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00160S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00160S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00160S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00160S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00160S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00160S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00160S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00160S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00160S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00A37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00A37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00A37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00A37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00A37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00A37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00A37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00A37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00A37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00A37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00A37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00A48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00A48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00A48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00A48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00A48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00A48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00A48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00A48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00A48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00A48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00A48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00A60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00A60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00A60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00A60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00A60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00A60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00A60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00A60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00A60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00A60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00A60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00B37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00B37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00B37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00B37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00B37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00B37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00B37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00B37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00B37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00B37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00B37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00B48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00B48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00B48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00B48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00B48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00B48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00B48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00B48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00B48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00B48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00B48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00B60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00B60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00B60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00B60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00B60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00B60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00B60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00B60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00B60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00B60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00B60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRM00C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRM00C37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00C37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00C37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRM00C37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00C37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00C37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00C37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00C37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00C37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00C37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00C37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRM00C48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00C48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00C48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRM00C48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00C48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00C48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00C48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00C48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00C48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00C48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00C48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRM00C60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00C60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00C60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRM00C60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00C60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00C60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00C60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00C60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00C60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00C60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRM00C60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMA9125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMA9C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMA9C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB1C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB1C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB2C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB2C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB3C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB3C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4130S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4130S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4130S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4130S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4130S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4130S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4130S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4130S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4130S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4130S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4130S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4A30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4A30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4A30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4A30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4A30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4A30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4A30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4A30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4A30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4A30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4A30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4B30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4B30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4B30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4B30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4B30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4B30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4B30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4B30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4B30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4B30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4B30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB4C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB4C30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4C30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4C30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB4C30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4C30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4C30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4C30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4C30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4C30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4C30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB4C30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5130S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5130S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5130S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5130S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5130S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5130S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5130S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5130S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5130S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5130S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5130S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5A30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5A30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5A30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5A30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5A30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5A30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5A30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5A30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5A30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5A30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5A30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5B30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5B30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5B30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5B30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5B30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5B30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5B30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5B30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5B30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5B30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5B30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB5C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB5C30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5C30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5C30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB5C30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5C30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5C30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5C30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5C30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5C30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5C30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB5C30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6130S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6130S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6130S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6130S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6130S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6130S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6130S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6130S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6130S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6130S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6130S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6A30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6A30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6A30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6A30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6A30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6A30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6A30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6A30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6A30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6A30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6A30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6B30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6B30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6B30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6B30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6B30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6B30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6B30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6B30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6B30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6B30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6B30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB6C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB6C30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6C30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6C30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB6C30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6C30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6C30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6C30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6C30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6C30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6C30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB6C30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7130S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7130S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7130S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7130S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7130S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7130S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7130S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7130S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7130S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7130S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7130S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7A30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7A30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7A30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7A30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7A30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7A30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7A30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7A30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7A30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7A30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7A30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7B30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7B30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7B30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7B30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7B30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7B30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7B30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7B30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7B30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7B30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7B30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | No heat
BVRMB7C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1000 | 600 - 1000 | Hot water Coil
BVRMB7C30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7C30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7C30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB7C30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7C30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7C30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7C30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7C30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7C30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7C30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB7C30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B7 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8137S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8137S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8137S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8137S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8137S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8137S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8137S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8137S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8137S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8137S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8137S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8A37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8A37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8A37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8A37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8A37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8A37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8A37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8A37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8A37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8A37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8A37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8B37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8B37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8B37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8B37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8B37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8B37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8B37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8B37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8B37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8B37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8B37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8C37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8C37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8C37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB8C37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8C37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8C37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8C37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8C37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8C37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8C37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB8C37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9131S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9131S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9131S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9131S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9131S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9131S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9131S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9131S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9131S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9131S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9131S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9137S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9137S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9137S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9137S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9137S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9137S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9137S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9137S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9137S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9137S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9137S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9142S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9142S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9142S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9142S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9142S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9142S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9142S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9142S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9142S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9142S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9142S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9A31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9A31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9A31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9A31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9A37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9A37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9A37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9A42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9A42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9A42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9A42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9A42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9A42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9A42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9A42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9A42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9A42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9A42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9B31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9B31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9B31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9B31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9B37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9B37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9B37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9B42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9B42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9B42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9B42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9B42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9B42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9B42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9B42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9B42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9B42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9B42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9C31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9C31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9C31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9C31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9C37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9C37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMB9C37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMB9C42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9C42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9C42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMB9C42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9C42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9C42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9C42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9C42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9C42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9C42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMB9C42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1131S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1131S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1131S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1131S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1131S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1131S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1131S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1131S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1131S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1131S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1131S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1137S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1137S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1137S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1137S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1137S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1137S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1137S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1137S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1137S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1137S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1137S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1142S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1142S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1142S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1142S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1142S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1142S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1142S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1142S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1142S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1142S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1142S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1A31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1A31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1A31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1A31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1A37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1A37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1A37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1A42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1A42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1A42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1A42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1A42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1A42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1A42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1A42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1A42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1A42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1A42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1B31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1B31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1B31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1B31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1B37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1B37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1B37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1B42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1B42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1B42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1B42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1B42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1B42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1B42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1B42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1B42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1B42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1B42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1C31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1C31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1C31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1C31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1C37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1C37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC1C37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC1C42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1C42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1C42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC1C42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1C42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1C42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1C42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1C42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1C42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1C42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC1C42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3131S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3131S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3131S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3131S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3131S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3131S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3131S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3131S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3131S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3131S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3131S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3137S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3137S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3137S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3137S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3137S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3137S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3137S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3137S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3137S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3137S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3137S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3142S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3142S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3142S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3142S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3142S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3142S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3142S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3142S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3142S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3142S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3142S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3148S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3148S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3148S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3148S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3148S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3148S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3148S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3148S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3148S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3148S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3148S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3A31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3A31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3A31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3A37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3A37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3A37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3A42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3A42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3A42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3A42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3A48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3A48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3A48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3A48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3B31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3B31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3B31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3B37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3B37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3B37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3B42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3B42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3B42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3B42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3B48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3B48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3B48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3B48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3C31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3C31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3C31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3C37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3C37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC3C37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC3C42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3C42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3C42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3C42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3C48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3C48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC3C48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC3C48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4131S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4131S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4131S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4131S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4131S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4131S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4131S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4131S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4131S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4131S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4131S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4137S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4137S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4137S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4137S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4137S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4137S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4137S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4137S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4137S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4137S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4137S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4142S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4142S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4142S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4142S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4142S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4142S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4142S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4142S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4142S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4142S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4142S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4148S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4148S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4148S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4148S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4148S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4148S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4148S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4148S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4148S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4148S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4148S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4A31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4A31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4A31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4A37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4A37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4A37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4A42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4A42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4A42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4A42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4A48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4A48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4A48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4A48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4B31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4B31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4B31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4B37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4B37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4B37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4B42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4B42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4B42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4B42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4B48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4B48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4B48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4B48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4C31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4C31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4C31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4C37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4C37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC4C37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC4C42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4C42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4C42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4C42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4C48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4C48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC4C48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC4C48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5131S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5131S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5131S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5131S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5131S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5131S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5131S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5131S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5131S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5131S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5131S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5137S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5137S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5137S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5137S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5137S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5137S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5137S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5137S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5137S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5137S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5137S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5142S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5142S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5142S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5142S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5142S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5142S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5142S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5142S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5142S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5142S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5142S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5148S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5148S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5148S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5148S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5148S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5148S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5148S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5148S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5148S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5148S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5148S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5160S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5160S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5160S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5160S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5160S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5160S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5160S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5160S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5160S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5160S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5160S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5A31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5A31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5A31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5A31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5A37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5A37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5A37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5A42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5A42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5A42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5A42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5A48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5A48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5A48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5A60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5A60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5A60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5A60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5A60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5A60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5A60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5A60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5A60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5A60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5A60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5B31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5B31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5B31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5B31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5B37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5B37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5B37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5B42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5B42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5B42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5B42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5B48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5B48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5B48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5B60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5B60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5B60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5B60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5B60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5B60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5B60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5B60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5B60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5B60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5B60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5C31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5C31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5C31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5C31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5C37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5C37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC5C37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC5C42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5C42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5C42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5C42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5C48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5C48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC5C48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC5C60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5C60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5C60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC5C60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5C60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5C60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5C60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5C60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5C60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5C60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC5C60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C5 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6131S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6131S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6131S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6131S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6131S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6131S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6131S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6131S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6131S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6131S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6131S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6137S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6137S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6137S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6137S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6137S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6137S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6137S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6137S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6137S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6137S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6137S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6142S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6142S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6142S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6142S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6142S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6142S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6142S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6142S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6142S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6142S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6142S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6148S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6148S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6148S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6148S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6148S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6148S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6148S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6148S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6148S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6148S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6148S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6160S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6160S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6160S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6160S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6160S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6160S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6160S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6160S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6160S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6160S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6160S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6A31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6A31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6A31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6A31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6A37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6A37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6A37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6A42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6A42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6A42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6A42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6A48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6A48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6A48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6A60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6A60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6A60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6A60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6A60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6A60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6A60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6A60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6A60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6A60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6A60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6B31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6B31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6B31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6B31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6B37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6B37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6B37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6B42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6B42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6B42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6B42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6B48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6B48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6B48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6B60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6B60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6B60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6B60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6B60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6B60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6B60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6B60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6B60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6B60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6B60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6C31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6C31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6C31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6C31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6C37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6C37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC6C37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC6C42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6C42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6C42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6C42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6C48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6C48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC6C48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC6C60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6C60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6C60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC6C60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6C60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6C60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6C60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6C60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6C60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6C60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC6C60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7131S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7131S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7131S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7131S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7131S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7131S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7131S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7131S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7131S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7131S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7131S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7137S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7137S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7137S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7137S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7137S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7137S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7137S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7137S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7137S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7137S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7137S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7142S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7142S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7142S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7142S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7142S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7142S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7142S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7142S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7142S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7142S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7142S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7148S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7148S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7148S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7148S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7148S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7148S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7148S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7148S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7148S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7148S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7148S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7160S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7160S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7160S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7160S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7160S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7160S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7160S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7160S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7160S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7160S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7160S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7A31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7A31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7A31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7A31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7A37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7A37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7A37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7A42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7A42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7A42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7A42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7A48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7A48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7A48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7A60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7A60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7A60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7A60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7A60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7A60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7A60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7A60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7A60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7A60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7A60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7B31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7B31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7B31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7B31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7B37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7B37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7B37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7B42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7B42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7B42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7B42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7B48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7B48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7B48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7B60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7B60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7B60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7B60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7B60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7B60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7B60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7B60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7B60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7B60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7B60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7C31S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7C31S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7C31S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7C31S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C31S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C31S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C31S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C31S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C31S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C31S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C31S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7C37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7C37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | No heat
BVRMC7C37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVRMC7C42S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 210 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7C42S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7C42S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7C42S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C42S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C42S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C42S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C42S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C42S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C42S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C42S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 210 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7C48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7C48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | No heat
BVRMC7C48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVRMC7C60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7C60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7C60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC7C60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7C60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7C60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7C60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7C60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7C60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7C60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC7C60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9160S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9160S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9160S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9160S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9160S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9160S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9160S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9160S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9160S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9160S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9160S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9A60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9A60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9A60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9A60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9A60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9A60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9A60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9A60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9A60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9A60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9A60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9B60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9B60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9B60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9B60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9B60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9B60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9B60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9B60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9B60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9B60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9B60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9C60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9C60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9C60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMC9C60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9C60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9C60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9C60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9C60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9C60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9C60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMC9C60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | C9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1160S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1160S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1160S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1160S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1160S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1160S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1160S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1160S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1160S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1160S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1160S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1A60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1A60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1A60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1A60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1A60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1A60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1A60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1A60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1A60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1A60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1A60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1B60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1B60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1B60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1B60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1B60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1B60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1B60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1B60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1B60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1B60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1B60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1C60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1C60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1C60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | No heat
BVRMD1C60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1C60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1C60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1C60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1C60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1C60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1C60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVRMD1C60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | D1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | Right-hand | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00137S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00137S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00137S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00137S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00137S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00137S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00137S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00137S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00137S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00137S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00137S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00148S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00148S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00148S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00148S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00148S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00148S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00148S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00148S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00148S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00148S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00148S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00160S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00160S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00160S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00160S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00160S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00160S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00160S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00160S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00160S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00160S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00160S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Piston (R-454B & R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00A37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00A37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00A37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00A37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00A37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00A37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00A37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00A37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00A37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00A37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00A37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00A48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00A48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00A48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00A48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00A48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00A48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00A48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00A48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00A48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00A48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00A48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00A60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00A60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00A60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00A60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00A60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00A60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00A60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00A60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00A60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00A60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00A60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00B37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00B37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00B37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00B37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00B37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00B37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00B37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00B37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00B37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00B37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00B37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00B48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00B48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00B48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00B48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00B48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00B48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00B48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00B48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00B48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00B48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00B48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00B60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00B60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00B60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00B60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00B60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00B60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00B60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00B60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00B60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00B60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00B60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOM00C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOM00C37S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 150 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00C37S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00C37S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOM00C37S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00C37S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00C37S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00C37S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00C37S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00C37S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00C37S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00C37S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 150 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOM00C48S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.5 | Not Applicable | 230 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00C48S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00C48S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | No heat
BVOM00C48S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00C48S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00C48S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00C48S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00C48S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00C48S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00C48S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00C48S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7 | Not Applicable | 230 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1000 - 1600 | 1100 - 1600 | Hot water Coil
BVOM00C60S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 4.3 | Not Applicable | 240 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00C60S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00C60S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | No heat
BVOM00C60S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00C60S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00C60S4P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00C60S4P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00C60S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00C60S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00C60S4N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOM00C60S4N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | 00 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | 4 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.6 | Not Applicable | 240 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 7/8 | 3/8 | 4 | No cooling coil | 1200 - 1850 | 1200 - 1850 | Hot water Coil
BVOMA9125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMA9C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMA9C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | A9 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB1C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB1C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B1 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB2C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB2C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B2 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB3C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB3C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B3 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4130S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4130S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4130S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4130S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4130S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4130S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4130S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4130S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4130S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4130S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4130S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4A30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4A30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4A30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4A30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4A30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4A30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4A30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4A30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4A30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4A30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4A30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4B30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4B30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4B30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4B30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4B30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4B30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4B30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4B30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4B30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4B30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4B30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB4C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB4C30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4C30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4C30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB4C30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4C30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4C30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4C30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4C30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4C30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4C30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB4C30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B4 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5130S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5130S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5130S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5130S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5130S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5130S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5130S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5130S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5130S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5130S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5130S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5A30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5A30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5A30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5A30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5A30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5A30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5A30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5A30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5A30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5A30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5A30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5B30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5B30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5B30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5B30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5B30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5B30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5B30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5B30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5B30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5B30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5B30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB5C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5C25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5C25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5C25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5C25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5C25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB5C30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5C30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5C30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB5C30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5C30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5C30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5C30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5C30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5C30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5C30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB5C30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B5 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6125S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6125S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6125S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6125S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6125S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6125S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6125S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6125S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6125S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6125S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6125S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6130S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB6130S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB6130S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB6130S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6130S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6130S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6130S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6130S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6130S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6130S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6130S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Piston (R-454B & R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6A25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6A25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6A25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6A25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6A25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6A25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6A25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6A25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6A25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6A25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6A25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6A30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB6A30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB6A30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB6A30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6A30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6A30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6A30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6A30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6A30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6A30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6A30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6B25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6B25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6B25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6B25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6B25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6B25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6B25S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6B25S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6B25S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6B25S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6B25S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6B30S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.7 | Not Applicable | 140 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB6B30S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB6B30S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | No heat
BVOMB6B30S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6B30S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6B30S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6B30S3P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6B30S2N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6B30S2N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 2 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6B30S3N3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6B30S3N4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 3 row hot water coil without Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.4 | Not Applicable | 140 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1200 | 1100 - 1200 | Hot water Coil
BVOMB6C25S001R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 208/240V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.4 | Not Applicable | 130 | 208/240 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6C25S003R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6C25S004R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | No heat | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | No heat
BVOMB6C25S2P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6C25S2P4R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 2 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. & 130°F aquastat | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil
BVOMB6C25S3P3R | B Series | Variable speed high eff. ECM motor | Multi-pos. | B6 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 3 row hot water coil with Pump &Valve | 120V, 60 Hz, 1 ph. | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 4.8 | Not Applicable | 130 | 120 V, 60 Hz, 1 Ph | Not Applicable | 40 VA, Class 2 | 3/4 | 3/8 | 4 | No cooling coil | 600 - 1000 | 600 - 1000 | Hot water Coil