## Front
SUBMITTAL DATA
F SERIES AIR HANDLER
Job: |  |  |  | Engineer:
Location: |  |  |  | Architect:
Schedule No.: |  |  |  | Date:
System Designation: |  |  |  | For:
FEATURES
Product Warranty
Optional Accessories
Unit Size
|  | FCME22118S004R | FCME22C30B152R | FEME31B18S003R | FEMUU1160B201A
Factory Installed Heat (kW) |  | none | 15kW | none | 20kW
Refrigerant |  | R-454B | R-454B | R-32 | R-410A
Factory Installed metering device |  | Piston | Bleed HP-A/C TXV | Non-bleed HP-A/C TXV | Piston
Blower Data: | Motor Type | 3-speed PSC motor | 3-speed PSC motor | 5-speed high eff. ECM motor | 5-speed high eff. ECM motor
| Motor H.P. | 1/5 | 1/3 | 1/3 | 1
| F.L.A. | 2 | 1.9 | 3.9 | 4.6
Nominal CFM |  | 600 | 1000 | 600 | 2000
Max Unit Weight (lbs) |  | 80 | 105 | 80 | 155
Available Voltages |  | 120 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph | 120 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph
Maximum Elec. Heat available (kW) |  | none | 15kW | none | 20kW
Transformer Size and Type |  | 40 VA, Class 2 | 40 VA, Class 2 | 40 VA, Class 2 | 40 VA, Class 2
Refrigerant Conn. (IDS) Suction |  | 3/4 | 7/8 | 3/4 | 7/8
Refrigerant Conn. (IDS) Liquid |  | 3/8 | 3/8 | 3/8 | 3/8
Pallet Quantity (min order per model) |  | 6 | 4 | 6 | 2
NOTES:
Cooling capacities subject to outdoor unit matchup. See http://www.adpnow.com/extratings/ for individual capacities by OEM
Cooling and Heating capacity data is rated at the following conditions:
Cooling: 80 FDB / 67 FWB Indoor, 95 FDB Outdoor
Heating: 70 FDB / 47 FWB Indoor, 43 FDB Outdoor
| A1 Refrigerants Product Nomenclature |  |  | A2L Refrigerants Product Nomenclature
2140 Lake Park Blvd., Richardson, TX 75080
www.adpnow.com
Available from factory as upflow or upflow/horizontal. Field installed horizontal drain pan kit also available.
Coils are air pressure tested at 500psi, leak tested with helium, sealed with rubber plugs, and then charged with dry air.
A1 model Suitable for use with R-22 and R-410A.
A2L model Suitable for use with R-32 and R-454B.
A2L model include factory installed Refrigerant Detections System (RDS).
Only four (4) screws to remove blower panel for easier access.
Available in copper or aluminum construction.
Dynamically balanced blowers for quiet, vibration-free operation.
Downflow kit available for field installation.
Piston or HP-A/C TXV available factory installed. Screw-on TXVs available as kits for field installation .
5-year limited warranty (Terms & Conditions Apply).
Product improvement is a continuous process at Advanced Distributor Products. Therefore, product specifications are subject to change without notice and without obligation on our part. Please contact your ADP representative or distributor to verify details.
© 2025 by Advanced Distributor Products. All rights reserved.

## Back
SUBMITTAL DATA
F SERIES LOW PROFILE AIR HANDLER
Dimensions | [10 empty] | Supply Duct Opening |  |  |  | Return Duct Opening |  |  |  | Pallet Qty.
Air Handler Size | [5 empty] | A (in) |  |  | B (in) | C (in) | Depth (in) |  | Width (in) |  | Depth (in) |  | Width (in) |  | (-S Option)
FCME22118S004R | [5 empty] | 36 |  |  | 22 | 15 | 17 |  | 13 |  | 20.35 |  | 12.2 |  | 6
FCME22C30B152R | [5 empty] | 41 |  |  | 22 | 18.5 | 17 |  | 16.5 |  | 20.35 |  | 16.2 |  | 4
FEME31B18S003R | [5 empty] | 36 |  |  | 22 | 15 | 17 |  | 13 |  | 20.35 |  | 12.2 |  | 6
FEMUU1160B201A | [5 empty] | 48 |  |  | 26 | 21.88 | 21 |  | 20 |  | 24.6 |  | 20.08 |  | 2
| Airflow (CFM) vs. External Static Pressure (inches W.C.) | [8 empty] | Electric Data
Unit Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5
FCME22118S004R | Low | 431 | 424 | 425 | 403 | 385
| *Med | 645 | 645 | 645 | 641 | 597
| High | 804 | 804 | 804 | 793 | 765
[10 empty] | Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size[3] (A)
Unit Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | [6 empty] | kW[1] | BTUH
FCME22C30B152R | Low | 867 | 839 | 803 | 780 | 733 | [6 empty] | 240 V[2] | 240 V[2] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| *Med | 1044 | 1015 | 991 | 941 | 889 |  |  |  | FCME22C30B152R | CKT 1 | 15[5] | 10 | 34121.42 | 2 | 1.9 | 47.6389 | 54.4583 | 50 | 60
| High | 1260 | 1234 | 1200 | 1149 | 1098 |  |  |  |  | CKT 2 | 15[5] | 5 | 17060.71 | 2 | 1.9 | 22.5694 | 26.0417 | 25 | 30
Unit Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6
FEME31B18S003R | 1 | 529 | 492 | 429 | 367 | 328 | 289
| 2 | 603 | 563 | 526 | 469 | 417 | 380
| *3 | 757 | 725 | 701 | 668 | 639 | 586
| 4 | 4 | 777 | 746 | 720 | 692 | 661 |  |  | Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size[3] (A)
| 5 | 5 | 826 | 798 | 768 | 745 | 720 | [5 empty] | kW[1] | BTUH
[13 empty] | 240 V[2] | 240 V[2] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
Unit Size | Tap | 0.1 | 0.2 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.6 | FEMUU1160B201A | CKT 1 | 20[6] | 10 | 34121.42 | 4.9 | 4.6 | 51.2639 | 57.8333 | 60 | 60
FEMUU1160B201A | 1 | 1394 | 1342 | 1288 | 1251 | 1172 | 1109 | 1077 | 1025 |  | CKT 2 | 20[6] | 10 | 34121.42 | 4.9 | 4.6 | 45.1389 | 52.0833 | 50 | 60
| 2 | 1722 | 1666 | 1623 | 1594 | 1564 | 1534 | 1518 | 1471
| *3 | 2083 | 2048 | 2013 | 1990 | 1972 | 1947 | 1929 | 1885 | Unit Size | Electric Heating Capacity |  | Blower Amps |  |  | Minimum Circuit Ampacity |  |  | Circuit Breaker Amps per Stage
| 4 | 2179 | 2135 | 2101 | 2079 | 2056 | 2039 | 2021 | 1937 |  | kW [1] | BTUH
| 5 | 2209 | 2166 | 2122 | 2101 | 2057 | 2058 | 2047 | 1956 |  | 240 V [2] | 240 V [2] | 120 V | 208 V | 240 V | 120 V | 208 V | 240 V | 1 | 2
- Speeds marked with asterisk are the factory speed settings for both heating and cooling. | [9 empty] | FCME22118S004R | 0 | 0 | 2 | 1.1605 | 1.1 | 2.5 | 1.4506 | 1.375 | 15 | -
[10 empty] | Unit Size | Electric Heating Capacity |  | Blower Amps |  |  | Minimum Circuit Ampacity |  |  | Circuit Breaker Amps per Stage
[11 empty] | kW [1] | BTUH
[11 empty] | 240 V [2] | 240 V [2] | 120 V | 208 V | 240 V | 120 V | 208 V | 240 V | 1 | 2
[10 empty] | FEME31B18S003R | 0 | 0 | 3.9 | 3.165 | 3 | 4.9 | 3.9562 | 3.75 | 15 | -
[1] kW packages in bold italics require and include circuit breakers; circuit breakers are optional for others.
[2] For 208 volt use 0.751 correction factor for kW & BTUH.
[3] Breaker supplied with heat kit may need to be changed. Verify breaker sizing based on min, circuit ampacity.
[4] 10 kW electric heat must not be used in downflow configuration
[5] 15 kW electric heat must be operated at high speed setting in downflow configuration
[6] 20 kW electric heat must be operated at medium speed setting in downflow configuration

## Nomenclature (hidden)
[7 empty] | F | C |  | M |  | E31 | 9 |  | 24 | S | 05 |  | 2 |  | A
[7 empty] | Series | Blower Motor |  | Airflow Config. |  | Slab No. | Metering Device |  | Unit Size | Line Voltage Connection | Electric Heat |  | Voltage |  | Revision | Revision
[7 empty] | F | C: | 3-speed PSC motor | M: | Multi-pos. (vertical, left or right horiz.) | E31 E32 E33 etc. | 1: | Piston (R-410A) | 18 24 25 30 31 36 37 42 48 60 | S = Stripped wire B = Circuit breaker | 00: | none (sizes 18-60) | 1: | 208/240 V, 60 Hz, 1 ph. (ECM only)
[8 empty] | E: | 5-speed high eff. ECM motor |  |  |  | 7: | Bleed HP-A/C TXV (R-410A) |  |  | 05: | 5kW (sizes 18-48) | 2: | 208/240 V, 60 Hz, 1 ph. (PSC only)
[13 empty] | 9: | Non-bleed HP-A/C TXV (R-410A) |  |  | 07: | 7.5kW (sizes 18-60) | 3: | 120 V, 60 Hz, 1 ph. (ECM only)
[17 empty] | 10: | 10kW (sizes 18-60) | 4: | 120 V, 60 Hz, 1 ph. (PSC only)
| Amount of Heat (kW) | [15 empty] | 15: | 15kW (sizes 30-60)
| 0 | 5 | 7.5 | 10 | 15 | 20 | [10 empty] | 20: | 20kW (sizes 48-60)
S | # | #
B |  | O | # | # | # | #
| #: | standard
| O: | optional
[7 empty] | F | C |  | M |  | E31 | 9 |  | 24 | S | 05 |  | 2 |  | R
[7 empty] | Series | Blower Motor |  | Airflow Config. |  | Slab No. | Metering Device |  | Unit Size | Line Voltage Connection | Electric Heat |  | Voltage |  | Refrigerant Detection System
[7 empty] | F | C: | 3-speed PSC motor | M: | Multi-pos. (vertical, left or right horiz.) | E31 E32 E33 etc. | 1: | Piston (R-454B & R-32) | 18 24 25 30 31 36 37 42 48 60 | S = Stripped wire B = Circuit breaker | 00: | none (sizes 18-60) | 1: | 208/240 V, 60 Hz, 1 ph. (ECM only) | R: | Included (Factory installed)
[8 empty] | E: | 5-speed high eff. ECM motor |  |  |  | A: | Non-bleed HP-A/C TXV (R-454B) |  |  | 05: | 5kW (sizes 18-48) | 2: | 208/240 V, 60 Hz, 1 ph. (PSC only)
[13 empty] | B: | Non-bleed HP-A/C TXV (R-32) |  |  | 07: | 7.5kW (sizes 18-60) | 3: | 120 V, 60 Hz, 1 ph. (ECM only)
[13 empty] | C: | Bleed HP-A/C TXV (R-454B) |  |  | 10: | 10kW (sizes 18-60) | 4: | 120 V, 60 Hz, 1 ph. (PSC only)
[17 empty] | 15: | 15kW (sizes 30-60)
[17 empty] | 20: | 20kW (sizes 48-60)

## Data (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Part Number | Series | Blower Motor | Airflow Config. | Slab No. | Metering Device | Unit Size | Line Voltage Connection | Electric Heat | Voltage | Revision | Refrigerant (R22 or R-410A) | Factory Installed metering device | Blower Data: Motor H.P. | Blower Data: F.L.A. @ 240 V | Nominal CFM | Max Unit Weight (lbs) | Available Voltages | Maximum Elec. Heat available (kW) | Transformer Size and Type | Refrigerant Conn. (IDS) Suction | Refrigerant Conn. (IDS) Liquid | Pallet Quantity (min order per model)
FCME22118S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22118S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22118S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22118B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22118B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22118B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22125S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22125S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22125S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22125B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22125B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22125B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22A25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22A36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22B25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22B36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22C25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22C36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME30118S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30118S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30118S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30118B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30118B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30118B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30A24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30B24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30C24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31125S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31125S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31125S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31125B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31125B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31125B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31A25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31A30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31B25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31B30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31C25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31C30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32118S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32118S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32118S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32118B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32118B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32118B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32125S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32125S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32125S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32125B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32125B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32125B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32A25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32A36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32B25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32B36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32C25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32C36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33A36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33B36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33C36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34A36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34B36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34C36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMBB8131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB8C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMG22118S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22118S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22118S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22118B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22118B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22118B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22125S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22125S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22125S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22125B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22125B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22125B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22A25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22A36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22B25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22B36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22C25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22C36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG30118S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30118S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30118S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30118B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30118B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30118B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30A24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30B24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30C24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31125S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31125S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31125S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31125B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31125B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31125B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31A25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31A30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31B25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31B30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31C25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31C30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32118S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32118S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32118S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32118B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32118B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32118B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32125S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32125S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32125S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32125B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32125B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32125B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32A25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32A36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32B25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32B36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C18S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C18S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C18S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C18B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C18B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C18B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C24S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C24S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C24S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C24B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C24B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C24B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32C25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32C36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33A36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33B36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33C36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34A36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34B36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C25S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C25S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C25S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C25B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C25B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C25B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C30S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C30S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C30S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C30B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C30B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C30B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C30B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C36S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C36S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C36S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C36B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C36B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C36B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34C36B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMSS8131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS8C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C31S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C31S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C31S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C31B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C31B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C31B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C31B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C37S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C37S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C37S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C37B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C37B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C37B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C37B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C42S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C42S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C42S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C42B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C42B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C42B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C42B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C48S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C48S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C48S052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C48B052R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C48B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C48B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C48B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C48B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1A60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1A60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1A60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1A60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1A60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1A60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1B60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1B60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1B60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1B60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1B60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1B60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1C60S002R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1C60S004R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1C60B072R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1C60B102R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1C60B152R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1C60B202R | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEME22118S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22118S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22118S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22118B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22118B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22118B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22125S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22125S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22125S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22125B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22125B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22125B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22A25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22A36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22B25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22B36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22C25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22C36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME30118S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30118S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30118S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30118B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30118B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30118B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30A24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30B24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30C24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31125S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31125S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31125S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31125B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31125B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31125B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31A25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31A30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31B25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31B30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31C25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31C30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32118S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32118S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32118S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32118B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32118B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32118B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32125S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32125S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32125S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32125B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32125B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32125B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32A25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32A36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32B25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32B36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32C25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32C36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33A36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33B36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33C36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34A36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34B36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34C36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMBB8131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB8C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMG22118S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22118S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22118S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22118B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22118B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22118B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22125S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22125S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22125S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22125B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22125B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22125B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22A25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22A36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22B25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22B36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22C25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22C36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG30118S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30118S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30118S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30118B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30118B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30118B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30A24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30B24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30C24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31125S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31125S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31125S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31125B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31125B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31125B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31A25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31A30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31B25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31B30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31C25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31C30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32118S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32118S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32118S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32118B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32118B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32118B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32125S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32125S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32125S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32125B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32125B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32125B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32A25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32A36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32B25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32B36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C18S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C18S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C18S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C18B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C18B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C18B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C24S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C24S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C24S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C24B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C24B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C24B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32C25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32C36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33A36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33B36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33C36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-454B & R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34A36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34B36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-32) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C25S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C25S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C25S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C25B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C25B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C25B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C30S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C30S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C30S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C30B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C30B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C30B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C30B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C36S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C36S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C36S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C36B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C36B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C36B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34C36B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-454B) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMSS8131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS8C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS8 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C31S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C31S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C31S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C31B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C31B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C31B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C31B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C37S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C37S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C37S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C37B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C37B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C37B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C37B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C42S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C42S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C42S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C42B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C42B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C42B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C42B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C48S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C48S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C48S051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C48B051R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C48B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C48B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C48B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C48B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-454B & R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1A60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1A60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1A60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1A60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1A60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1A60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1B60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1B60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1B60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1B60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1B60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1B60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-32) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1C60S001R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1C60S003R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1C60B071R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1C60B101R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1C60B151R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1C60B201R | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-454B) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCME22118S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22118S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22118S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22118B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22118B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22118B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22124B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22125S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22125S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22125S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22125B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22125B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22125B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22130B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22136B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22718S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22718S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22718S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22718B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22718B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22718B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22724S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22724S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22724S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22724B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22724B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22724B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22725S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22725S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22725S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22725B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22725B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22725B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22730S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22730S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22730S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22730B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22730B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22730B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22730B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22736S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22736S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22736S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22736B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22736B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22736B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22736B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22918S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22918S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22918S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22918B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22918B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22918B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22924S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22924S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22924S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22924B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22924B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22924B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME22925S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22925S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22925S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22925B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22925B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22925B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22930S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22930S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22930S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22930B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22930B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22930B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22930B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22936S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22936S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22936S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22936B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22936B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22936B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME22936B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME30118S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30118S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30118S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30118B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30118B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30118B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30124B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30718S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30718S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30718S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30718B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30718B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30718B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30724S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30724S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30724S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30724B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30724B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30724B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30918S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30918S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30918S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30918B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30918B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30918B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30924S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30924S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30924S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30924B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30924B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME30924B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31118B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31124B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31125S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31125S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31125S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31125B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31125B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31125B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31130B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31718S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31718S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31718S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31718B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31718B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31718B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31724S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31724S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31724S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31724B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31724B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31724B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31725S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31725S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31725S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31725B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31725B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31725B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31730S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31730S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31730S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31730B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31730B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31730B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31730B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31918S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31918S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31918S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31918B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31918B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31918B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31924S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31924S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31924S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31924B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31924B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31924B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME31925S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31925S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31925S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31925B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31925B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31925B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31930S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31930S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31930S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31930B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31930B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31930B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME31930B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32118S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32118S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32118S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32118B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32118B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32118B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32124B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32125S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32125S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32125S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32125B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32125B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32125B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32130B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32136B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32718S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32718S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32718S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32718B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32718B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32718B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32724S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32724S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32724S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32724B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32724B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32724B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32725S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32725S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32725S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32725B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32725B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32725B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32730S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32730S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32730S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32730B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32730B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32730B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32730B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32736S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32736S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32736S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32736B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32736B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32736B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32736B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32918S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32918S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32918S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32918B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32918B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32918B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32924S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32924S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32924S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32924B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32924B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32924B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCME32925S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32925S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32925S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32925B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32925B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32925B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32930S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32930S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32930S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32930B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32930B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32930B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32930B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32936S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32936S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32936S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32936B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32936B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32936B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME32936B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33125B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33130B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33136B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33725S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33725S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33725S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33725B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33725B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33725B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33730S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33730S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33730S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33730B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33730B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33730B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33730B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33736S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33736S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33736S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33736B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33736B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33736B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33736B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33925S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33925S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33925S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33925B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33925B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33925B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33930S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33930S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33930S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33930B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33930B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33930B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33930B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33936S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33936S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33936S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33936B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33936B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33936B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME33936B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34125B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34130B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34136B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34725S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34725S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34725S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34725B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34725B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34725B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34730S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34730S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34730S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34730B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34730B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34730B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34730B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34736S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34736S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34736S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34736B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34736B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34736B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34736B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34925S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34925S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34925S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34925B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34925B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34925B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34930S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34930S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34930S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34930B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34930B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34930B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34930B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34936S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34936S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34936S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34936B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34936B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34936B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCME34936B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMCC3131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC3960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC6960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC9960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMBB9948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC1948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC4960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMCC7960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMDD1960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMG22118S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22118S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22118S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22118B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22118B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22118B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22124B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22125S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22125S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22125S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22125B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22125B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22125B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22130B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22136B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22718S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22718S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22718S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22718B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22718B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22718B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22724S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22724S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22724S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22724B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22724B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22724B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22725S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22725S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22725S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22725B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22725B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22725B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22730S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22730S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22730S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22730B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22730B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22730B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22730B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22736S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22736S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22736S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22736B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22736B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22736B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22736B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22918S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22918S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22918S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22918B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22918B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22918B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22924S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22924S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22924S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22924B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22924B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22924B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG22925S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22925S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22925S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22925B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22925B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22925B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22930S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22930S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22930S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22930B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22930B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22930B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22930B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22936S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22936S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22936S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22936B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22936B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22936B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG22936B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG30118S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30118S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30118S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30118B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30118B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30118B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30124B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30718S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30718S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30718S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30718B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30718B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30718B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30724S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30724S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30724S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30724B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30724B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30724B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30918S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30918S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30918S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30918B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30918B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30918B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30924S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30924S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30924S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30924B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30924B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG30924B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31118B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31124B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31125S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31125S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31125S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31125B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31125B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31125B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31130B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31718S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31718S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31718S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31718B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31718B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31718B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31724S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31724S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31724S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31724B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31724B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31724B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31725S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31725S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31725S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31725B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31725B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31725B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31730S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31730S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31730S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31730B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31730B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31730B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31730B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31918S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31918S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31918S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31918B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31918B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31918B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31924S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31924S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31924S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31924B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31924B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31924B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG31925S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31925S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31925S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31925B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31925B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31925B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31930S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31930S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31930S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31930B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31930B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31930B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG31930B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32118S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32118S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32118S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32118B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32118B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32118B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32124B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32125S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32125S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32125S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32125B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32125B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32125B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32130B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32136B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32718S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32718S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32718S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32718B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32718B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32718B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32724S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32724S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32724S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32724B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32724B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32724B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32725S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32725S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32725S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32725B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32725B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32725B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32730S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32730S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32730S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32730B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32730B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32730B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32730B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32736S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32736S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32736S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32736B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32736B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32736B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32736B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32918S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32918S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 2 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32918S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32918B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32918B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32918B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/5 | 1.1 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32924S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32924S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32924S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32924B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32924B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32924B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.6 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FCMG32925S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32925S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32925S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32925B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32925B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32925B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32930S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32930S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32930S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32930B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32930B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32930B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32930B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32936S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32936S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32936S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32936B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32936B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32936B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG32936B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33125B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33130B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33136B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33725S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33725S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33725S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33725B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33725B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33725B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33730S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33730S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33730S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33730B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33730B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33730B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33730B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33736S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33736S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33736S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33736B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33736B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33736B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33736B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33925S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33925S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33925S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33925B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33925B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33925B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33930S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33930S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33930S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33930B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33930B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33930B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33930B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33936S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33936S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33936S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33936B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33936B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33936B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG33936B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34125B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34130B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34136B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34725S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34725S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34725S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34725B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34725B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34725B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34730S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34730S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34730S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34730B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34730B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34730B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34730B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34736S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34736S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34736S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34736B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34736B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34736B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34736B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34925S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34925S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34925S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34925B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34925B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34925B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34930S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34930S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.2 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34930S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34930B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34930B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34930B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34930B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34936S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34936S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34936S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34936B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34936B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34936B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMG34936B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FCMTT3131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT3960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT6960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT9960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMSS9948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT1948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT4960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7131B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7137B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7142B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7148B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7731S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7731S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7731S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7731B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7731B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7731B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7731B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7737S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7737S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7737S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7737B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7737B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7737B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7737B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7742S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7742S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7742S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7742B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7742B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7742B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7742B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7748S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7748S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7748S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7748B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7748B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7748B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7748B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7748B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7931S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7931S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7931S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7931B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7931B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7931B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7931B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.6 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7937S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7937S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 5.3 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7937S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7937B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7937B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7937B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7937B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7942S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7942S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 8.5 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7942S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7942B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7942B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7942B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7942B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7948S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7948S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 7.5 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7948S052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7948B052A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7948B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7948B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7948B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7948B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMTT7960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1160B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1760S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1760S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1760B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1760B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1760B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1760B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1960S002A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1960S004A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 10.5 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1960B072A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1960B102A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1960B152A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FCMUU1960B202A | F Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3.9 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEME22118S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22118S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22118S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22118B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22118B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22118B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22124B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22125S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22125S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22125S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22125B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22125B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22125B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22130B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22136B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22718S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22718S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22718S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22718B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22718B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22718B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22724S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22724S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22724S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22724B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22724B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22724B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22725S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22725S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22725S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22725B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22725B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22725B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22730S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22730S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22730S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22730B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22730B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22730B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22730B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22736S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22736S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22736S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22736B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22736B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22736B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22736B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22918S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22918S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22918S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22918B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22918B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22918B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22924S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22924S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22924S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22924B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22924B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22924B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME22925S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22925S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22925S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22925B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22925B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22925B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22930S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22930S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22930S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22930B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22930B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22930B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22930B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22936S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22936S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22936S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22936B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22936B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22936B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME22936B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME30118S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30118S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30118S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30118B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30118B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30118B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30124B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30718S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30718S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30718S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30718B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30718B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30718B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30724S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30724S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30724S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30724B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30724B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30724B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30918S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30918S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30918S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30918B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30918B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30918B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30924S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30924S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30924S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30924B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30924B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME30924B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31118B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31124B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31125S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31125S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31125S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31125B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31125B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31125B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31130B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31718S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31718S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31718S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31718B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31718B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31718B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31724S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31724S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31724S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31724B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31724B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31724B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31725S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31725S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31725S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31725B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31725B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31725B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31730S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31730S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31730S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31730B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31730B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31730B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31730B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31918S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31918S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31918S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31918B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31918B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31918B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31924S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31924S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31924S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31924B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31924B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31924B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME31925S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31925S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31925S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31925B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31925B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31925B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31930S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31930S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31930S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31930B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31930B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31930B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME31930B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32118S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32118S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32118S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32118B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32118B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32118B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32124B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32125S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32125S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32125S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32125B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32125B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32125B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32130B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32136B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32718S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32718S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32718S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32718B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32718B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32718B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32724S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32724S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32724S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32724B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32724B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32724B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32725S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32725S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32725S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32725B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32725B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32725B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32730S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32730S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32730S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32730B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32730B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32730B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32730B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32736S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32736S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32736S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32736B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32736B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32736B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32736B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32918S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32918S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32918S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32918B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32918B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32918B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32924S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32924S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32924S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32924B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32924B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32924B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEME32925S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32925S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32925S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32925B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32925B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32925B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32930S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32930S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32930S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32930B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32930B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32930B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32930B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32936S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32936S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32936S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32936B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32936B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32936B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME32936B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33125B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33130B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33136B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33725S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33725S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33725S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33725B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33725B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33725B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33730S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33730S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33730S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33730B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33730B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33730B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33730B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33736S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33736S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33736S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33736B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33736B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33736B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33736B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33925S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33925S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33925S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33925B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33925B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33925B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33930S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33930S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33930S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33930B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33930B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33930B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33930B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33936S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33936S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33936S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33936B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33936B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33936B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME33936B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34125B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34130B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34136B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34725S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34725S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34725S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34725B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34725B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34725B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34730S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34730S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34730S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34730B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34730B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34730B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34730B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34736S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34736S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34736S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34736B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34736B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34736B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34736B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34925S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34925S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34925S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34925B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34925B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34925B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34930S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34930S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34930S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34930B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34930B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34930B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34930B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34936S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34936S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34936S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34936B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34936B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34936B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEME34936B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | E34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMCC3131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC3960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC6960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC9960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMBB9948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | BB9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC1948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC4960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMCC7960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | CC7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMDD1960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | DD1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMG22118S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22118S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22118S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22118B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22118B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22118B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22124B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22125S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22125S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22125S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22125B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22125B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22125B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22130B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22136B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22718S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22718S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22718S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22718B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22718B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22718B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22724S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22724S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22724S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22724B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22724B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22724B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22725S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22725S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22725S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22725B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22725B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22725B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22730S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22730S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22730S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22730B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22730B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22730B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22730B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22736S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22736S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22736S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22736B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22736B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22736B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22736B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22918S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22918S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22918S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22918B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22918B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22918B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22924S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22924S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22924S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22924B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22924B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22924B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG22925S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22925S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22925S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22925B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22925B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22925B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22930S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22930S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22930S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22930B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22930B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22930B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22930B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22936S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22936S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22936S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22936B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22936B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22936B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG22936B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G22 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG30118S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30118S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30118S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30118B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30118B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30118B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30124B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30718S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30718S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30718S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30718B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30718B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30718B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30724S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30724S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30724S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30724B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30724B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30724B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30918S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30918S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30918S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30918B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30918B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30918B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30924S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30924S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30924S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30924B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30924B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG30924B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G30 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31118B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31124B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31125S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31125S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31125S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31125B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31125B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31125B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31130B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31718S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31718S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31718S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31718B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31718B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31718B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31724S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31724S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31724S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31724B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31724B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31724B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31725S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31725S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31725S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31725B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31725B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31725B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31730S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31730S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31730S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31730B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31730B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31730B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31730B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31918S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31918S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31918S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31918B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31918B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31918B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31924S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31924S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31924S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31924B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31924B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31924B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG31925S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31925S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31925S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31925B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31925B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31925B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31930S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31930S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31930S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31930B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31930B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31930B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG31930B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G31 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32118S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32118S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32118S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32118B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32118B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32118B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32124B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32125S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32125S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32125S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32125B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32125B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32125B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32130B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32136B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32718S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32718S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32718S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32718B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32718B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32718B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32724S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32724S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32724S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32724B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32724B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32724B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32725S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32725S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32725S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32725B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32725B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32725B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32730S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32730S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32730S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32730B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32730B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32730B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32730B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32736S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32736S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32736S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32736B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32736B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32736B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32736B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32918S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32918S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 600 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32918S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32918B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32918B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32918B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 18 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 600 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32924S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32924S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3.9 | 800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32924S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32924B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32924B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32924B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 24 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 3 | 800 | 80 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 3/4 | 3/8 | 6
FEMG32925S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32925S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32925S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32925B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32925B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32925B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32930S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32930S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32930S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32930B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32930B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32930B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32930B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32936S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32936S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32936S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32936B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32936B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32936B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG32936B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G32 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33125B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33130B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33136B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33725S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33725S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33725S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33725B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33725B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33725B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33730S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33730S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33730S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33730B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33730B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33730B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33730B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33736S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33736S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33736S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33736B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33736B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33736B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33736B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33925S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33925S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33925S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33925B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33925B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33925B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33930S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33930S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33930S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33930B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33930B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33930B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33930B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33936S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33936S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33936S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33936B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33936B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33936B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG33936B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G33 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34125B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34130B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34136B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Piston (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34725S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34725S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34725S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34725B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34725B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34725B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34730S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34730S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34730S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34730B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34730B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34730B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34730B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34736S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34736S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34736S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34736B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34736B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34736B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34736B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34925S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34925S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34925S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34925B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34925B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34925B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 25 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 800 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34930S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34930S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34930S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34930B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34930B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34930B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34930B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 30 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34936S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34936S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34936S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34936B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34936B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34936B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMG34936B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | G34 | Non-bleed HP-A/C TXV (R-410A) | 36 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 105 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 4
FEMTT3131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT3960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT3 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT6960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT6 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT9960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT9 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMSS9948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | SS9 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT1948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT1 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT4960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT4 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7131B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7137B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7142B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7148B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7731S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7731S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7731S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7731B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7731B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7731B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7731B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7737S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7737S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7737S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7737B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7737B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7737B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7737B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7742S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7742S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7742S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7742B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7742B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7742B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7742B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7748S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7748S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7748S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7748B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7748B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7748B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7748B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7748B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7931S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7931S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7931S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7931B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7931B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7931B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7931B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 31 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1000 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7937S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7937S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1200 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7937S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7937B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7937B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7937B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7937B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 37 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1200 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7942S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7942S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 5.8 | 1400 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7942S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7942B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7942B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7942B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7942B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 42 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 3 | 1400 | 155 | 208/240 V, 60 Hz, 1 Ph | 15kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7948S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7948S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 8.7 | 1600 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7948S051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Stripped wire | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7948B051A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7948B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7948B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7948B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7948B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 48 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 3/4 | 3.2 | 1600 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMTT7960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | TT7 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1160B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Piston (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1760S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1760S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1760B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1760B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1760B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1760B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1960S001A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1960S003A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 11.1 | 2000 | 155 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1960B071A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1960B101A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1960B151A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 15kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2
FEMUU1960B201A | F Series | 5-speed high eff. ECM motor | Multi-pos. (vertical, left or right horiz.) | UU1 | Non-bleed HP-A/C TXV (R-410A) | 60 | Circuit breaker | 20kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1 | 4.6 | 2000 | 155 | 208/240 V, 60 Hz, 1 Ph | 20kW | 40 VA, Class 2 | 7/8 | 3/8 | 2

## Airflow (hidden)
[20 empty] | 120 Volt 3-Speed PSC Motor | [6 empty] | 120 Volt 5-Speed High Efficiency | [7 empty] | 208/240 Volt 5-Speed High Efficiency
[13 empty] | Airflow (CFM) vs. External Static Pressure (inches W.C.) | [6 empty] | Airflow (CFM) vs. External Static Pressure (inches W.C.) | [6 empty] | Airflow (CFM) vs. External Static Pressure (inches W.C.) | [7 empty] | Airflow (CFM) vs. External Static Pressure (inches W.C.)
ID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | Size | Tap | 0.1 | 0.2 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.6 | Voltage/Motor
18_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 18 | Low | 505 | 499 | 487 | 434 | 397 |  |  |  | 18 | Low | 505 | 499 | 487 | 434 | 397 | 18 | Low | 431 | 424 | 425 | 403 | 385 | 18 | 1 | 529 | 492 | 429 | 367 | 328 | 289 | 18 | 1 | 492 | 448 | 393 | 361 | 361 | 333 | 307 | 273 | 208/240 V, 60 Hz, 1 ph. (PSC only) | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5
18_208/240 V, 60 Hz, 1 ph. (PSC only)_2 |  | Med | 653 | 634 | 625 | 600 | 512 |  |  |  |  | Med | 653 | 634 | 625 | 600 | 512 |  | *Med | 645 | 645 | 645 | 641 | 597 | 18 | 2 | 603 | 563 | 526 | 469 | 417 | 380 | 18 | 2 | 513 | 471 | 420 | 414 | 384 | 357 | 325 | 318 | 120 V, 60 Hz, 1 ph. (PSC only) | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5
18_208/240 V, 60 Hz, 1 ph. (PSC only)_3 |  | *High | 891 | 853 | 812 | 778 | 733 |  |  |  |  | *High | 891 | 853 | 812 | 778 | 733 |  | High | 804 | 804 | 804 | 793 | 765 | 18 | *3 | 757 | 725 | 701 | 668 | 639 | 586 | 18 | *3 | 667 | 641 | 615 | 605 | 596 | 577 | 567 | 560 | 208/240 V, 60 Hz, 1 ph. (ECM only) | Tap | 0.1 | 0.2 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.6
24_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 24 | Low | 663 | 624 | 583 | 578 | 562 |  |  |  | 24 | Low | 663 | 624 | 583 | 578 | 562 | 24 | Low | 530 | 525 | 519 | 507 | 483 | 18 | 4 | 806 | 777 | 746 | 720 | 692 | 661 | 18 | 4 | 705 | 673 | 665 | 648 | 630 | 621 | 603 | 590 | 120 V, 60 Hz, 1 ph. (ECM only) | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6
24_208/240 V, 60 Hz, 1 ph. (PSC only)_2 |  | Med | 902 | 864 | 822 | 792 | 744 |  |  |  |  | Med | 902 | 864 | 822 | 792 | 744 |  | *Med | 925 | 915 | 875 | 823 | 736 | 18 | 5 | 849 | 826 | 798 | 768 | 745 | 720 | 18 | 5 | 721 | 689 | 673 | 656 | 639 | 629 | 612 | 590
24_208/240 V, 60 Hz, 1 ph. (PSC only)_3 |  | *High | 1159 | 1097 | 1031 | 960 | 893 |  |  |  |  | *High | 1159 | 1097 | 1031 | 960 | 893 |  | High | 1189 | 1110 | 1016 | 917 | 826 | 24 | 1 | 613 | 575 | 538 | 487 | 432 | 395 | 24 | 1 | 732 | 627 | 590 | 581 | 571 | 545 | 536 | 525
25_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 25 | *Low | 867 | 839 | 803 | 780 | 733 |  |  |  | 25 | *Low | 867 | 839 | 803 | 780 | 733 | 25 | *Low | 998 | 956 | 905 | 844 | 770 | 24 | 2 | 769 | 737 | 711 | 678 | 648 | 594 | 24 | 2 | 671 | 634 | 594 | 578 | 573 | 546 | 493 | 480
25_208/240 V, 60 Hz, 1 ph. (PSC only)_2 |  | Med | 1044 | 1015 | 991 | 941 | 889 |  |  |  |  | Med | 1044 | 1015 | 991 | 941 | 889 |  | Med | 1045 | 1004 | 962 | 871 | 785 | 24 | *3 | 955 | 926 | 899 | 871 | 842 | 814 | 24 | *3 | 892 | 859 | 832 | 828 | 818 | 797 | 790 | 775
25_208/240 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1260 | 1234 | 1200 | 1149 | 1098 |  |  |  |  | High | 1260 | 1234 | 1200 | 1149 | 1098 |  | High | 1089 | 1036 | 980 | 905 | 826 | 24 | 4 | 989 | 962 | 938 | 912 | 891 | 865 | 24 | 4 | 911 | 866 | 839 | 832 | 825 | 818 | 804 | 760
30_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 30 | Low | 867 | 839 | 803 | 780 | 733 |  |  |  | 30 | Low | 867 | 839 | 803 | 780 | 733 | 30 | Low | 998 | 956 | 905 | 844 | 770 | 24 | 5 | 1046 | 1024 | 996 | 971 | 945 | 919 | 24 | 5 | 924 | 886 | 846 | 832 | 825 | 818 | 797 | 780
30_208/240 V, 60 Hz, 1 ph. (PSC only)_2 |  | *Med | 1044 | 1015 | 991 | 941 | 889 |  |  |  |  | *Med | 1044 | 1015 | 991 | 941 | 889 |  | *Med | 1045 | 1004 | 962 | 871 | 785 | 25 | 1 | 687 | 633 | 573 | 482 | 424 | 373 | 25 | 1 | 732 | 627 | 590 | 581 | 571 | 545 | 536 | 525
30_208/240 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1260 | 1234 | 1200 | 1149 | 1098 |  |  |  |  | High | 1260 | 1234 | 1200 | 1149 | 1098 |  | High | 1089 | 1036 | 980 | 905 | 826 | 25 | 2 | 830 | 794 | 757 | 708 | 636 | 570 | 25 | 2 | 671 | 634 | 594 | 578 | 573 | 546 | 493 | 480
31_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 31 | *Low | 1143 | 1112 | 1081 | 1047 | 1015 |  |  |  | 31 | *Low | 1143 | 1112 | 1081 | 1047 | 1015 | 31 | *Low | 1008 | 1004 | 972 | 925 | 867 | 25 | *3 | 971 | 948 | 913 | 882 | 840 | 802 | 25 | *3 | 892 | 859 | 832 | 828 | 818 | 797 | 790 | 775
31_208/240 V, 60 Hz, 1 ph. (PSC only)_2 |  | Med | 1268 | 1233 | 1186 | 1165 | 1133 |  |  |  |  | Med | 1268 | 1233 | 1186 | 1165 | 1133 |  | Med | 1190 | 1150 | 1100 | 1040 | 970 | 25 | 4 | 1012 | 988 | 960 | 922 | 889 | 849 | 25 | 4 | 911 | 866 | 839 | 832 | 825 | 818 | 804 | 760
31_208/240 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1415 | 1390 | 1352 | 1314 | 1260 |  |  |  |  | High | 1415 | 1390 | 1352 | 1314 | 1260 |  | High | 1250 | 1200 | 1140 | 1070 | 995 | 25 | 5 | 1057 | 1040 | 1011 | 979 | 943 | 909 | 25 | 5 | 924 | 886 | 846 | 832 | 825 | 818 | 797 | 780
36_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 36 | Low | 1143 | 1112 | 1081 | 1047 | 1015 |  |  |  | 36 | Low | 1143 | 1112 | 1081 | 1047 | 1015 | 36 | Low | 945 | 930 | 912 | 869 | 793 | 30 | 1 | 765 | 720 | 667 | 602 | 521 | 474 | 30 | 1 | 871 | 830 | 778 | 722 | 671 | 635 | 625 | 586
36_208/240 V, 60 Hz, 1 ph. (PSC only)_2 |  | *Med | 1268 | 1233 | 1186 | 1165 | 1133 |  |  |  |  | *Med | 1268 | 1233 | 1186 | 1165 | 1133 |  | *Med | 1150 | 1145 | 1123 | 1166 | 1004 | 30 | 2 | 971 | 950 | 913 | 879 | 836 | 797 | 30 | 2 | 906 | 859 | 809 | 779 | 715 | 689 | 654 | 635
36_208/240 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1415 | 1390 | 1352 | 1314 | 1260 |  |  |  |  | High | 1415 | 1390 | 1352 | 1314 | 1260 |  | High | 1291 | 1291 | 1285 | 1277 | 1200 | 30 | *3 | 1163 | 1141 | 1116 | 1090 | 1054 | 1025 | 30 | *3 | 1085 | 1070 | 1048 | 1036 | 1024 | 1001 | 989 | 975
37_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 37 | *Low | 1318 | 1299 | 1270 | 1210 | 1147 |  |  |  | 37 | *Low | 1318 | 1299 | 1270 | 1210 | 1147 | 37 | Low | 1008 | 1004 | 972 | 925 | 867 | 30 | 4 | 1203 | 1189 | 1168 | 1139 | 1112 | 1078 | 30 | 4 | 1125 | 1103 | 1087 | 1059 | 1047 | 1024 | 1012 | 983
37_208/240 V, 60 Hz, 1 ph. (PSC only)_2 |  | Med | 1444 | 1409 | 1374 | 1294 | 1220 |  |  |  |  | Med | 1444 | 1409 | 1374 | 1294 | 1220 |  | *Med | 1190 | 1150 | 1100 | 1040 | 970 | 30 | 5 | 1222 | 1202 | 1188 | 1161 | 1128 | 1102 | 30 | 5 | 1176 | 1146 | 1114 | 1098 | 1081 | 1059 | 1047 | 1029
37_208/240 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1712 | 1645 | 1544 | 1453 | 1328 |  |  |  |  | High | 1712 | 1645 | 1544 | 1453 | 1328 |  | High | 1250 | 1200 | 1140 | 1070 | 995 | 31 | 1 | 853 | 793 | 724 | 658 | 525 | 475 | 31 | 1 | 871 | 830 | 778 | 722 | 671 | 635 | 625 | 586
42_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 42 | Low | 1318 | 1299 | 1270 | 1210 | 1147 |  |  |  | 42 | Low | 1318 | 1299 | 1270 | 1210 | 1147 | 42 | *Low | 1393 | 1378 | 1366 | 1246 | 1167 | 31 | 2 | 1047 | 999 | 948 | 898 | 840 | 785 | 31 | 2 | 906 | 859 | 809 | 779 | 715 | 689 | 654 | 635
42_208/240 V, 60 Hz, 1 ph. (PSC only)_2 |  | *Med | 1444 | 1409 | 1374 | 1294 | 1220 |  |  |  |  | *Med | 1444 | 1409 | 1374 | 1294 | 1220 |  | Med | 1603 | 1592 | 1575 | 1540 | 1443 | 31 | *3 | 1230 | 1185 | 1142 | 1104 | 1054 | 1007 | 31 | *3 | 1085 | 1070 | 1048 | 1036 | 1024 | 1001 | 989 | 975
42_208/240 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1712 | 1645 | 1544 | 1453 | 1328 |  |  |  |  | High | 1712 | 1645 | 1544 | 1453 | 1328 |  | High | 1811 | 1811 | 1805 | 1744 | 1674 | 31 | 4 | 1268 | 1231 | 1189 | 1147 | 1106 | 1053 | 31 | 4 | 1125 | 1103 | 1087 | 1059 | 1047 | 1024 | 1012 | 983
48_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 48 ** | *Low | 1764 | 1709 | 1652 | 1563 | 1418 |  |  |  | 48 ** | *Low | 1764 | 1709 | 1652 | 1563 | 1418 | 48 | Low | 1393 | 1378 | 1366 | 1246 | 1167 | 31 | 5 | 1316 | 1273 | 1237 | 1196 | 1152 | 1108 | 31 | 5 | 1176 | 1146 | 1114 | 1098 | 1081 | 1059 | 1047 | 1029
48_208/240 V, 60 Hz, 1 ph. (PSC only)_2 |  | Med | 1984 | 1884 | 1780 | 1683 | 1509 |  |  |  |  | Med | 1984 | 1884 | 1780 | 1683 | 1509 |  | *Med | 1603 | 1592 | 1575 | 1540 | 1443 | 36 | 1 | 835 | 798 | 761 | 710 | 629 | 569 | 36 | 1 | 882 | 887 | 826 | 804 | 766 | 760 | 755 | 695
48_208/240 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 2031 | 1959 | 1832 | 1725 | 1617 |  |  |  |  | High | 2031 | 1959 | 1832 | 1725 | 1617 |  | High | 1811 | 1811 | 1805 | 1744 | 1674 | 36 | 2 | 1158 | 1137 | 1114 | 1088 | 1054 | 1024 | 36 | 2 | 1082 | 1037 | 1025 | 1002 | 990 | 959 | 921 | 881
60_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 60 | Low | 1764 | 1709 | 1652 | 1563 | 1418 |  |  |  | 60 | Low | 1764 | 1709 | 1652 | 1563 | 1418 | 60 | Low | 1583 | 1583 | 1583 | 1567 | 1551 | 36 | *3 | 1354 | 1327 | 1310 | 1290 | 1270 | 1239 | 36 | *3 | 1270 | 1250 | 1238 | 1228 | 1214 | 1189 | 1179 | 1162
60_208/240 V, 60 Hz, 1 ph. (PSC only)_2 |  | Med | 1984 | 1884 | 1780 | 1683 | 1509 |  |  |  |  | Med | 1984 | 1884 | 1780 | 1683 | 1509 |  | *Med | 1972 | 1972 | 1968 | 1882 | 1819 | 36 | 4 | 1418 | 1389 | 1369 | 1351 | 1327 | 1304 | 36 | 4 | 1290 | 1275 | 1265 | 1246 | 1236 | 1227 | 1212 | 1172
60_208/240 V, 60 Hz, 1 ph. (PSC only)_3 |  | *High | 2031 | 1959 | 1832 | 1725 | 1617 |  |  |  |  | *High | 2031 | 1959 | 1832 | 1725 | 1617 |  | High | 2169 | 2146 | 2096 | 2004 | 1908 | 36 | 5 | 1429 | 1412 | 1395 | 1379 | 1358 | 1330 | 36 | 5 | 1335 | 1315 | 1301 | 1287 | 1278 | 1259 | 1240 | 1225
_ | [10 empty] | ** Use only low speed on heating for unit size 48 with 5kW electric heat. | [13 empty] | 37 | 1 | 908 | 851 | 794 | 730 | 632 | 535 | 37 | 1 | 882 | 887 | 826 | 804 | 766 | 760 | 755 | 695
18_120 V, 60 Hz, 1 ph. (PSC only)_1 | 18 | Low | 431 | 424 | 425 | 403 | 385 | [17 empty] | 37 | 2 | 1232 | 1186 | 1142 | 1104 | 1054 | 1005 | 37 | 2 | 1082 | 1037 | 1025 | 1002 | 990 | 959 | 921 | 881
18_120 V, 60 Hz, 1 ph. (PSC only)_2 |  | *Med | 645 | 645 | 645 | 641 | 597 | [17 empty] | 37 | *3 | 1432 | 1389 | 1346 | 1307 | 1272 | 1228 | 37 | *3 | 1270 | 1250 | 1238 | 1228 | 1214 | 1189 | 1179 | 1162
18_120 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 804 | 804 | 804 | 793 | 765 | [17 empty] | 37 | 4 | 1468 | 1426 | 1388 | 1350 | 1311 | 1275 | 37 | 4 | 1290 | 1275 | 1265 | 1246 | 1236 | 1227 | 1212 | 1172
24_120 V, 60 Hz, 1 ph. (PSC only)_1 | 24 | Low | 530 | 525 | 519 | 507 | 483 | [17 empty] | 37 | 5 | 1504 | 1474 | 1438 | 1401 | 1363 | 1323 | 37 | 5 | 1335 | 1315 | 1301 | 1287 | 1278 | 1259 | 1240 | 1225
24_120 V, 60 Hz, 1 ph. (PSC only)_2 |  | *Med | 925 | 915 | 875 | 823 | 736 | [17 empty] | 42 | 1 | 961 | 914 | 857 | 794 | 744 | 611 | 42 | 1 | 1008 | 907 | 861 | 832 | 803 | 772 | 717 | 671
24_120 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1189 | 1110 | 1016 | 917 | 826 | [17 empty] | 42 | 2 | 1417 | 1377 | 1339 | 1299 | 1267 | 1223 | 42 | 2 | 1292 | 1243 | 1202 | 1192 | 1171 | 1149 | 1127 | 1070
25_120 V, 60 Hz, 1 ph. (PSC only)_1 | 25 | *Low | 998 | 956 | 905 | 844 | 770 | [17 empty] | 42 | *3 | 1613 | 1574 | 1543 | 1508 | 1482 | 1447 | 42 | *3 | 1447 | 1430 | 1404 | 1377 | 1359 | 1340 | 1322 | 1283
25_120 V, 60 Hz, 1 ph. (PSC only)_2 |  | Med | 1045 | 1004 | 962 | 871 | 785 | [17 empty] | 42 | 4 | 1669 | 1634 | 1600 | 1564 | 1530 | 1504 | 42 | 4 | 1534 | 1502 | 1476 | 1459 | 1433 | 1416 | 1398 | 1362
25_120 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1089 | 1036 | 980 | 905 | 826 | [17 empty] | 42 | 5 | 1694 | 1665 | 1637 | 1603 | 1570 | 1537 | 42 | 5 | 1559 | 1519 | 1502 | 1477 | 1460 | 1434 | 1417 | 1381
30_120 V, 60 Hz, 1 ph. (PSC only)_1 | 30 | Low | 998 | 956 | 905 | 844 | 770 | [17 empty] | 48 | 1 | 1169 | 1106 | 1008 | 930 | 859 | 799 | 48 | 1 | 1585 | 1494 | 1320 | 1252 | 1210 | 1151 | 1120 | 1088
30_120 V, 60 Hz, 1 ph. (PSC only)_2 |  | *Med | 1045 | 1004 | 962 | 871 | 785 | [17 empty] | 48 | 2 | 1658 | 1615 | 1575 | 1532 | 1477 | 1409 | 48 | 2 | 1510 | 1463 | 1414 | 1389 | 1363 | 1324 | 1256 | 1228
30_120 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1089 | 1036 | 980 | 905 | 826 | [17 empty] | 48 | *3 | 1830 | 1792 | 1754 | 1737 | 1682 | 1622 | 48 | *3 | 1675 | 1633 | 1579 | 1556 | 1545 | 1510 | 1487 | 1451
31_120 V, 60 Hz, 1 ph. (PSC only)_1 | 31 | *Low | 1008 | 1004 | 972 | 925 | 867 | [17 empty] | 48 | 4 | 1863 | 1844 | 1809 | 1778 | 1740 | 1684 | 48 | 4 | 1737 | 1697 | 1655 | 1633 | 1612 | 1590 | 1568 | 1545
31_120 V, 60 Hz, 1 ph. (PSC only)_2 |  | Med | 1190 | 1150 | 1100 | 1040 | 970 | [17 empty] | 48 | 5 | 1895 | 1855 | 1836 | 1805 | 1772 | 1714 | 48 | 5 | 1781 | 1731 | 1679 | 1658 | 1637 | 1615 | 1593 | 1571
31_120 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1250 | 1200 | 1140 | 1070 | 995 | [17 empty] | 60 | 1 | 1317 | 1298 | 1239 | 1162 | 1049 | 972 | 60 | 1 | 1394 | 1342 | 1288 | 1251 | 1172 | 1109 | 1077 | 1025
36_120 V, 60 Hz, 1 ph. (PSC only)_1 | 36 | Low | 945 | 930 | 912 | 869 | 793 | [17 empty] | 60 | 2 | 1809 | 1752 | 1706 | 1707 | 1671 | 1619 | 60 | 2 | 1722 | 1666 | 1623 | 1594 | 1564 | 1534 | 1518 | 1471
36_120 V, 60 Hz, 1 ph. (PSC only)_2 |  | *Med | 1150 | 1145 | 1123 | 1166 | 1004 | [17 empty] | 60 | *3 | 1905 | 1851 | 1822 | 1784 | 1795 | 1756 | 60 | *3 | 2083 | 2048 | 2013 | 1990 | 1972 | 1947 | 1929 | 1885
36_120 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1291 | 1291 | 1285 | 1277 | 1200 | [17 empty] | 60 | 4 | 2013 | 1956 | 1908 | 1867 | 1890 | 1867 | 60 | 4 | 2179 | 2135 | 2101 | 2079 | 2056 | 2039 | 2021 | 1937
37_120 V, 60 Hz, 1 ph. (PSC only)_1 | 37 | Low | 1008 | 1004 | 972 | 925 | 867 | [17 empty] | 60 | 5 | 2230 | 2171 | 2119 | 2072 | 2038 | 2048 | 60 | 5 | 2209 | 2166 | 2122 | 2101 | 2057 | 2058 | 2047 | 1956
37_120 V, 60 Hz, 1 ph. (PSC only)_2 |  | *Med | 1190 | 1150 | 1100 | 1040 | 970
37_120 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1250 | 1200 | 1140 | 1070 | 995
42_120 V, 60 Hz, 1 ph. (PSC only)_1 | 42 | *Low | 1393 | 1378 | 1366 | 1246 | 1167
42_120 V, 60 Hz, 1 ph. (PSC only)_2 |  | Med | 1603 | 1592 | 1575 | 1540 | 1443
42_120 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1811 | 1811 | 1805 | 1744 | 1674
48_120 V, 60 Hz, 1 ph. (PSC only)_1 | 48 | Low | 1393 | 1378 | 1366 | 1246 | 1167
48_120 V, 60 Hz, 1 ph. (PSC only)_2 |  | *Med | 1603 | 1592 | 1575 | 1540 | 1443
48_120 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 1811 | 1811 | 1805 | 1744 | 1674
60_120 V, 60 Hz, 1 ph. (PSC only)_1 | 60 | Low | 1583 | 1583 | 1583 | 1567 | 1551
60_120 V, 60 Hz, 1 ph. (PSC only)_2 |  | *Med | 1972 | 1972 | 1968 | 1882 | 1819
60_120 V, 60 Hz, 1 ph. (PSC only)_3 |  | High | 2169 | 2146 | 2096 | 2004 | 1908
_
18_120 V, 60 Hz, 1 ph. (ECM only)_1 | 18 | 1 | 529 | 492 | 429 | 367 | 328 | 289
18_120 V, 60 Hz, 1 ph. (ECM only)_2 | 18 | 2 | 603 | 563 | 526 | 469 | 417 | 380
18_120 V, 60 Hz, 1 ph. (ECM only)_3 | 18 | *3 | 757 | 725 | 701 | 668 | 639 | 586
18_120 V, 60 Hz, 1 ph. (ECM only)_4 | 18 | 4 | 806 | 777 | 746 | 720 | 692 | 661
18_120 V, 60 Hz, 1 ph. (ECM only)_5 | 18 | 5 | 849 | 826 | 798 | 768 | 745 | 720
24_120 V, 60 Hz, 1 ph. (ECM only)_1 | 24 | 1 | 613 | 575 | 538 | 487 | 432 | 395
24_120 V, 60 Hz, 1 ph. (ECM only)_2 | 24 | 2 | 769 | 737 | 711 | 678 | 648 | 594
24_120 V, 60 Hz, 1 ph. (ECM only)_3 | 24 | *3 | 955 | 926 | 899 | 871 | 842 | 814
24_120 V, 60 Hz, 1 ph. (ECM only)_4 | 24 | 4 | 989 | 962 | 938 | 912 | 891 | 865
24_120 V, 60 Hz, 1 ph. (ECM only)_5 | 24 | 5 | 1046 | 1024 | 996 | 971 | 945 | 919
25_120 V, 60 Hz, 1 ph. (ECM only)_1 | 25 | 1 | 687 | 633 | 573 | 482 | 424 | 373
25_120 V, 60 Hz, 1 ph. (ECM only)_2 | 25 | 2 | 830 | 794 | 757 | 708 | 636 | 570
25_120 V, 60 Hz, 1 ph. (ECM only)_3 | 25 | *3 | 971 | 948 | 913 | 882 | 840 | 802
25_120 V, 60 Hz, 1 ph. (ECM only)_4 | 25 | 4 | 1012 | 988 | 960 | 922 | 889 | 849
25_120 V, 60 Hz, 1 ph. (ECM only)_5 | 25 | 5 | 1057 | 1040 | 1011 | 979 | 943 | 909
30_120 V, 60 Hz, 1 ph. (ECM only)_1 | 30 | 1 | 765 | 720 | 667 | 602 | 521 | 474
30_120 V, 60 Hz, 1 ph. (ECM only)_2 | 30 | 2 | 971 | 950 | 913 | 879 | 836 | 797
30_120 V, 60 Hz, 1 ph. (ECM only)_3 | 30 | *3 | 1163 | 1141 | 1116 | 1090 | 1054 | 1025
30_120 V, 60 Hz, 1 ph. (ECM only)_4 | 30 | 4 | 1203 | 1189 | 1168 | 1139 | 1112 | 1078
30_120 V, 60 Hz, 1 ph. (ECM only)_5 | 30 | 5 | 1222 | 1202 | 1188 | 1161 | 1128 | 1102
31_120 V, 60 Hz, 1 ph. (ECM only)_1 | 31 | 1 | 853 | 793 | 724 | 658 | 525 | 475
31_120 V, 60 Hz, 1 ph. (ECM only)_2 | 31 | 2 | 1047 | 999 | 948 | 898 | 840 | 785
31_120 V, 60 Hz, 1 ph. (ECM only)_3 | 31 | *3 | 1230 | 1185 | 1142 | 1104 | 1054 | 1007
31_120 V, 60 Hz, 1 ph. (ECM only)_4 | 31 | 4 | 1268 | 1231 | 1189 | 1147 | 1106 | 1053
31_120 V, 60 Hz, 1 ph. (ECM only)_5 | 31 | 5 | 1316 | 1273 | 1237 | 1196 | 1152 | 1108
36_120 V, 60 Hz, 1 ph. (ECM only)_1 | 36 | 1 | 835 | 798 | 761 | 710 | 629 | 569
36_120 V, 60 Hz, 1 ph. (ECM only)_2 | 36 | 2 | 1158 | 1137 | 1114 | 1088 | 1054 | 1024
36_120 V, 60 Hz, 1 ph. (ECM only)_3 | 36 | *3 | 1354 | 1327 | 1310 | 1290 | 1270 | 1239
36_120 V, 60 Hz, 1 ph. (ECM only)_4 | 36 | 4 | 1418 | 1389 | 1369 | 1351 | 1327 | 1304
36_120 V, 60 Hz, 1 ph. (ECM only)_5 | 36 | 5 | 1429 | 1412 | 1395 | 1379 | 1358 | 1330
37_120 V, 60 Hz, 1 ph. (ECM only)_1 | 37 | 1 | 908 | 851 | 794 | 730 | 632 | 535
37_120 V, 60 Hz, 1 ph. (ECM only)_2 | 37 | 2 | 1232 | 1186 | 1142 | 1104 | 1054 | 1005
37_120 V, 60 Hz, 1 ph. (ECM only)_3 | 37 | *3 | 1432 | 1389 | 1346 | 1307 | 1272 | 1228
37_120 V, 60 Hz, 1 ph. (ECM only)_4 | 37 | 4 | 1468 | 1426 | 1388 | 1350 | 1311 | 1275
37_120 V, 60 Hz, 1 ph. (ECM only)_5 | 37 | 5 | 1504 | 1474 | 1438 | 1401 | 1363 | 1323
42_120 V, 60 Hz, 1 ph. (ECM only)_1 | 42 | 1 | 961 | 914 | 857 | 794 | 744 | 611
42_120 V, 60 Hz, 1 ph. (ECM only)_2 | 42 | 2 | 1417 | 1377 | 1339 | 1299 | 1267 | 1223
42_120 V, 60 Hz, 1 ph. (ECM only)_3 | 42 | *3 | 1613 | 1574 | 1543 | 1508 | 1482 | 1447
42_120 V, 60 Hz, 1 ph. (ECM only)_4 | 42 | 4 | 1669 | 1634 | 1600 | 1564 | 1530 | 1504
42_120 V, 60 Hz, 1 ph. (ECM only)_5 | 42 | 5 | 1694 | 1665 | 1637 | 1603 | 1570 | 1537
48_120 V, 60 Hz, 1 ph. (ECM only)_1 | 48 | 1 | 1169 | 1106 | 1008 | 930 | 859 | 799
48_120 V, 60 Hz, 1 ph. (ECM only)_2 | 48 | 2 | 1658 | 1615 | 1575 | 1532 | 1477 | 1409
48_120 V, 60 Hz, 1 ph. (ECM only)_3 | 48 | *3 | 1830 | 1792 | 1754 | 1737 | 1682 | 1622
48_120 V, 60 Hz, 1 ph. (ECM only)_4 | 48 | 4 | 1863 | 1844 | 1809 | 1778 | 1740 | 1684
48_120 V, 60 Hz, 1 ph. (ECM only)_5 | 48 | 5 | 1895 | 1855 | 1836 | 1805 | 1772 | 1714
60_120 V, 60 Hz, 1 ph. (ECM only)_1 | 60 | 1 | 1317 | 1298 | 1239 | 1162 | 1049 | 972
60_120 V, 60 Hz, 1 ph. (ECM only)_2 | 60 | 2 | 1809 | 1752 | 1706 | 1707 | 1671 | 1619
60_120 V, 60 Hz, 1 ph. (ECM only)_3 | 60 | *3 | 1905 | 1851 | 1822 | 1784 | 1795 | 1756
60_120 V, 60 Hz, 1 ph. (ECM only)_4 | 60 | 4 | 2013 | 1956 | 1908 | 1867 | 1890 | 1867
60_120 V, 60 Hz, 1 ph. (ECM only)_5 | 60 | 5 | 2230 | 2171 | 2119 | 2072 | 2038 | 2048
_
18_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 18 | 1 | 492 | 448 | 393 | 361 | 361 | 333 | 307 | 273
18_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 18 | 2 | 513 | 471 | 420 | 414 | 384 | 357 | 325 | 318
18_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 18 | *3 | 667 | 641 | 615 | 605 | 596 | 577 | 567 | 560
18_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 18 | 4 | 705 | 673 | 665 | 648 | 630 | 621 | 603 | 590
18_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 18 | 5 | 721 | 689 | 673 | 656 | 639 | 629 | 612 | 590
24_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 24 | 1 | 732 | 627 | 590 | 581 | 571 | 545 | 536 | 525
24_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 24 | 2 | 671 | 634 | 594 | 578 | 573 | 546 | 493 | 480
24_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 24 | *3 | 892 | 859 | 832 | 828 | 818 | 797 | 790 | 775
24_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 24 | 4 | 911 | 866 | 839 | 832 | 825 | 818 | 804 | 760
24_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 24 | 5 | 924 | 886 | 846 | 832 | 825 | 818 | 797 | 780
25_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 25 | 1 | 732 | 627 | 590 | 581 | 571 | 545 | 536 | 525
25_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 25 | 2 | 671 | 634 | 594 | 578 | 573 | 546 | 493 | 480
25_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 25 | *3 | 892 | 859 | 832 | 828 | 818 | 797 | 790 | 775
25_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 25 | 4 | 911 | 866 | 839 | 832 | 825 | 818 | 804 | 760
25_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 25 | 5 | 924 | 886 | 846 | 832 | 825 | 818 | 797 | 780
30_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 30 | 1 | 871 | 830 | 778 | 722 | 671 | 635 | 625 | 586
30_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 30 | 2 | 906 | 859 | 809 | 779 | 715 | 689 | 654 | 635
30_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 30 | *3 | 1085 | 1070 | 1048 | 1036 | 1024 | 1001 | 989 | 975
30_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 30 | 4 | 1125 | 1103 | 1087 | 1059 | 1047 | 1024 | 1012 | 983
30_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 30 | 5 | 1176 | 1146 | 1114 | 1098 | 1081 | 1059 | 1047 | 1029
31_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 31 | 1 | 871 | 830 | 778 | 722 | 671 | 635 | 625 | 586
31_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 31 | 2 | 906 | 859 | 809 | 779 | 715 | 689 | 654 | 635
31_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 31 | *3 | 1085 | 1070 | 1048 | 1036 | 1024 | 1001 | 989 | 975
31_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 31 | 4 | 1125 | 1103 | 1087 | 1059 | 1047 | 1024 | 1012 | 983
31_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 31 | 5 | 1176 | 1146 | 1114 | 1098 | 1081 | 1059 | 1047 | 1029
36_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 36 | 1 | 882 | 887 | 826 | 804 | 766 | 760 | 755 | 695
36_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 36 | 2 | 1082 | 1037 | 1025 | 1002 | 990 | 959 | 921 | 881
36_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 36 | *3 | 1270 | 1250 | 1238 | 1228 | 1214 | 1189 | 1179 | 1162
36_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 36 | 4 | 1290 | 1275 | 1265 | 1246 | 1236 | 1227 | 1212 | 1172
36_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 36 | 5 | 1335 | 1315 | 1301 | 1287 | 1278 | 1259 | 1240 | 1225
37_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 37 | 1 | 882 | 887 | 826 | 804 | 766 | 760 | 755 | 695
37_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 37 | 2 | 1082 | 1037 | 1025 | 1002 | 990 | 959 | 921 | 881
37_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 37 | *3 | 1270 | 1250 | 1238 | 1228 | 1214 | 1189 | 1179 | 1162
37_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 37 | 4 | 1290 | 1275 | 1265 | 1246 | 1236 | 1227 | 1212 | 1172
37_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 37 | 5 | 1335 | 1315 | 1301 | 1287 | 1278 | 1259 | 1240 | 1225
42_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 42 | 1 | 1008 | 907 | 861 | 832 | 803 | 772 | 717 | 671
42_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 42 | 2 | 1292 | 1243 | 1202 | 1192 | 1171 | 1149 | 1127 | 1070
42_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 42 | *3 | 1447 | 1430 | 1404 | 1377 | 1359 | 1340 | 1322 | 1283
42_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 42 | 4 | 1534 | 1502 | 1476 | 1459 | 1433 | 1416 | 1398 | 1362
42_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 42 | 5 | 1559 | 1519 | 1502 | 1477 | 1460 | 1434 | 1417 | 1381
48_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 48 | 1 | 1585 | 1494 | 1320 | 1252 | 1210 | 1151 | 1120 | 1088
48_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 48 | 2 | 1510 | 1463 | 1414 | 1389 | 1363 | 1324 | 1256 | 1228
48_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 48 | *3 | 1675 | 1633 | 1579 | 1556 | 1545 | 1510 | 1487 | 1451
48_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 48 | 4 | 1737 | 1697 | 1655 | 1633 | 1612 | 1590 | 1568 | 1545
48_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 48 | 5 | 1781 | 1731 | 1679 | 1658 | 1637 | 1615 | 1593 | 1571
60_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 60 | 1 | 1394 | 1342 | 1288 | 1251 | 1172 | 1109 | 1077 | 1025
60_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 60 | 2 | 1722 | 1666 | 1623 | 1594 | 1564 | 1534 | 1518 | 1471
60_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 60 | *3 | 2083 | 2048 | 2013 | 1990 | 1972 | 1947 | 1929 | 1885
60_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 60 | 4 | 2179 | 2135 | 2101 | 2079 | 2056 | 2039 | 2021 | 1937
60_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 60 | 5 | 2209 | 2166 | 2122 | 2101 | 2057 | 2058 | 2047 | 1956

## Electrial data (hidden)
No Electric Heat
| Unit Size | Electric Heating Capacity |  | Blower Amps |  |  | Minimum Circuit Ampacity |  |  | Circuit Breaker Amps per Stage
|  | kW [1] | BTUH
|  | 240 V [2] | 240 V [2] | 120 V | 208 V | 240 V | 120 V | 208 V | 240 V | 1 | 2
3-speed PSC motor_18_none_1 | 18 | 0 | 0 | 2 | 1.1605 | 1.1 | 2.5 | 1.4506 | 1.375 | 15 | -
3-speed PSC motor_24_none_1 | 24 | 0 | 0 | 3.2 | 1.688 | 1.6 | 4 | 2.11 | 2 | 15 | -
3-speed PSC motor_25_none_1 | 25 | 0 | 0 | 3.2 | 2.0045 | 1.9 | 4 | 2.5056 | 2.375 | 15 | -
3-speed PSC motor_30_none_1 | 30 | 0 | 0 | 3.2 | 2.0045 | 1.9 | 4 | 2.5056 | 2.375 | 15 | -
3-speed PSC motor_31_none_1 | 31 | 0 | 0 | 5.3 | 2.743 | 2.6 | 6.625 | 3.4287 | 3.25 | 15 | -
3-speed PSC motor_36_none_1 | 36 | 0 | 0 | 5.3 | 2.743 | 2.6 | 6.625 | 3.4287 | 3.25 | 15 | -
3-speed PSC motor_37_none_1 | 37 | 0 | 0 | 5.3 | 2.0045 | 1.9 | 6.625 | 2.5056 | 2.375 | 15 | -
3-speed PSC motor_42_none_1 | 42 | 0 | 0 | 8.5 | 2.0045 | 1.9 | 10.625 | 2.5056 | 2.375 | 15 | -
3-speed PSC motor_48_none_1 | 48 | 0 | 0 | 7.5 | 4.1145 | 3.9 | 9.375 | 5.1431 | 4.875 | 15 | -
3-speed PSC motor_60_none_1 | 60 | 0 | 0 | 10.5 | 4.1145 | 3.9 | 13.125 | 5.1431 | 4.875 | 15 | -
5-speed high eff. ECM motor_18_none_1 | 18 | 0 | 0 | 3.9 | 3.165 | 3 | 4.9 | 3.9562 | 3.75 | 15 | -
5-speed high eff. ECM motor_24_none_1 | 24 | 0 | 0 | 3.9 | 3.165 | 3 | 4.9 | 3.9562 | 3.75 | 15 | -
5-speed high eff. ECM motor_25_none_1 | 25 | 0 | 0 | 5.8 | 3.2 | 3 | 7.3 | 4 | 3.8 | 15 | -
5-speed high eff. ECM motor_30_none_1 | 30 | 0 | 0 | 5.8 | 3.165 | 3 | 7.3 | 3.9562 | 3.75 | 15 | -
5-speed high eff. ECM motor_31_none_1 | 31 | 0 | 0 | 5.8 | 3.165 | 3 | 7.3 | 3.9562 | 3.75 | 15 | -
5-speed high eff. ECM motor_36_none_1 | 36 | 0 | 0 | 5.8 | 3.165 | 3 | 7.3 | 3.9562 | 3.75 | 15 | -
5-speed high eff. ECM motor_37_none_1 | 37 | 0 | 0 | 5.8 | 3.165 | 3 | 7.3 | 3.9562 | 3.75 | 15 | -
5-speed high eff. ECM motor_42_none_1 | 42 | 0 | 0 | 5.8 | 3.165 | 3 | 7.3 | 3.9562 | 3.75 | 15 | -
5-speed high eff. ECM motor_48_none_1 | 48 | 0 | 0 | 8.7 | 3.376 | 3.2 | 10.9 | 4.22 | 4 | 15 | -
5-speed high eff. ECM motor_60_none_1 | 60 | 0 | 0 | 11.1 | 4.853 | 4.6 | 13.9 | 6.0663 | 5.75 | 15 | -
Electric Data
| Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size[3] (A)
|  |  |  | kW[1] | BTUH
|  |  |  | 240 V[2] | 240 V[2] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
3-speed PSC motor_18_5kW_1 | 18 | CKT 1 | 5 | 5 | 17060.71 | 1.2 | 1.1 | 24.0694 | 27.4167 | 25 | 30
3-speed PSC motor_18_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 1.2 | 1.1 | 35.3542 | 40.4375 | 40 | 45
3-speed PSC motor_18_10kW_1 |  | CKT 1 | 10[4] | 10 | 34121.42 | 1.2 | 1.1 | 46.6389 | 53.4583 | 50 | 60
3-speed PSC motor_24_5kW_1 | 24 | CKT 1 | 5 | 5 | 17060.71 | 1.7 | 1.6 | 24.6944 | 28.0417 | 25 | 30
3-speed PSC motor_24_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 1.7 | 1.6 | 35.9792 | 41.0625 | 40 | 45
3-speed PSC motor_24_10kW_1 |  | CKT 1 | 10[4] | 10 | 34121.42 | 1.7 | 1.6 | 47.2639 | 54.0833 | 50 | 60
3-speed PSC motor_25_5kW_1 | 25 | CKT 1 | 5 | 5 | 17060.71 | 2 | 1.9 | 25.0694 | 28.4167 | 30 | 30
3-speed PSC motor_25_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 2 | 1.9 | 36.3542 | 41.4375 | 40 | 45
3-speed PSC motor_25_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 2 | 1.9 | 47.6389 | 54.4583 | 50 | 60
3-speed PSC motor_30_5kW_1 | 30 | CKT 1 | 5 | 5 | 17060.71 | 2 | 1.9 | 25.0694 | 28.4167 | 30 | 30
3-speed PSC motor_30_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 2 | 1.9 | 36.3542 | 41.4375 | 40 | 45
3-speed PSC motor_30_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 2 | 1.9 | 47.6389 | 54.4583 | 50 | 60
3-speed PSC motor_30_15kW_1 |  | CKT 1 | 15[5] | 10 | 34121.42 | 2 | 1.9 | 47.6389 | 54.4583 | 50 | 60
3-speed PSC motor_30_15kW_2 |  | CKT 2 | 15[5] | 5 | 17060.71 | 2 | 1.9 | 22.5694 | 26.0417 | 25 | 30
3-speed PSC motor_31_5kW_1 | 31 | CKT 1 | 5 | 5 | 17060.71 | 2.7 | 2.6 | 25.9444 | 29.2917 | 30 | 30
3-speed PSC motor_31_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 2.7 | 2.6 | 37.2292 | 42.3125 | 40 | 45
3-speed PSC motor_31_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 2.7 | 2.6 | 48.5139 | 55.3333 | 50 | 60
3-speed PSC motor_31_15kW_1 |  | CKT 1 | 15[5] | 10 | 34121.42 | 2.7 | 2.6 | 48.5139 | 55.3333 | 50 | 60
3-speed PSC motor_31_15kW_2 |  | CKT 2 | 15[5] | 5 | 17060.71 | 2.7 | 2.6 | 22.5694 | 26.0417 | 25 | 30
3-speed PSC motor_36_5kW_1 | 36 | CKT 1 | 5 | 5 | 17060.71 | 2.7 | 2.6 | 25.9444 | 29.2917 | 30 | 30
3-speed PSC motor_36_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 2.7 | 2.6 | 37.2292 | 42.3125 | 40 | 45
3-speed PSC motor_36_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 2.7 | 2.6 | 48.5139 | 55.3333 | 50 | 60
3-speed PSC motor_36_15kW_1 |  | CKT 1 | 15[5] | 10 | 34121.42 | 2.7 | 2.6 | 48.5139 | 55.3333 | 50 | 60
3-speed PSC motor_36_15kW_2 |  | CKT 2 | 15[5] | 5 | 17060.71 | 2.7 | 2.6 | 22.5694 | 26.0417 | 25 | 30
3-speed PSC motor_37_5kW_1 | 37 | CKT 1 | 5 | 5 | 17060.71 | 2 | 1.9 | 25.0694 | 28.4167 | 30 | 30
3-speed PSC motor_37_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 2 | 1.9 | 36.3542 | 41.4375 | 40 | 45
3-speed PSC motor_37_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 2 | 1.9 | 47.6389 | 54.4583 | 50 | 60
3-speed PSC motor_37_15kW_1 |  | CKT 1 | 15 | 10 | 34121.42 | 2 | 1.9 | 47.6389 | 54.4583 | 50 | 60
3-speed PSC motor_37_15kW_2 |  | CKT 2 | 15 | 5 | 17060.71 | 2 | 1.9 | 22.5694 | 26.0417 | 25 | 30
3-speed PSC motor_42_5kW_1 | 42 | CKT 1 | 5 | 5 | 17060.71 | 2 | 1.9 | 25.0694 | 28.4167 | 30 | 30
3-speed PSC motor_42_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 2 | 1.9 | 36.3542 | 41.4375 | 40 | 45
3-speed PSC motor_42_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 2 | 1.9 | 47.6389 | 54.4583 | 50 | 60
3-speed PSC motor_42_15kW_1 |  | CKT 1 | 15 | 10 | 34121.42 | 2 | 1.9 | 47.6389 | 54.4583 | 50 | 60
3-speed PSC motor_42_15kW_2 |  | CKT 2 | 15 | 5 | 17060.71 | 2 | 1.9 | 22.5694 | 26.0417 | 25 | 30
3-speed PSC motor_48_5kW_1 | 48 | CKT 1 | 5 | 5 | 17060.71 | 4.1 | 3.9 | 27.6944 | 30.9167 | 30 | 35
3-speed PSC motor_48_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 4.1 | 3.9 | 38.9792 | 43.9375 | 40 | 45
3-speed PSC motor_48_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 4.1 | 3.9 | 50.2639 | 56.9583 | 60 | 60
3-speed PSC motor_48_15kW_1 |  | CKT 1 | 15 | 10 | 34121.42 | 4.1 | 3.9 | 50.2639 | 56.9583 | 60 | 60
3-speed PSC motor_48_15kW_2 |  | CKT 2 | 15 | 5 | 17060.71 | 4.1 | 3.9 | 22.5694 | 26.0417 | 25 | 30
3-speed PSC motor_48_20kW_1 |  | CKT 1 | 20[6] | 10 | 34121.42 | 4.1 | 3.9 | 50.2639 | 56.9583 | 60 | 60
3-speed PSC motor_48_20kW_2 |  | CKT 2 | 20[6] | 10 | 34121.42 | 4.1 | 3.9 | 45.1389 | 52.0833 | 50 | 60
3-speed PSC motor_60_7.5kw_1 | 60 | CKT 1 | 7.5 | 7.5 | 25591.065 | 4.1 | 3.9 | 38.9792 | 43.9375 | 40 | 45
3-speed PSC motor_60_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 4.1 | 3.9 | 50.2639 | 56.9583 | 60 | 60
3-speed PSC motor_60_15kW_1 |  | CKT 1 | 15 | 10 | 34121.42 | 4.1 | 3.9 | 50.2639 | 56.9583 | 60 | 60
3-speed PSC motor_60_15kW_2 |  | CKT 2 | 15 | 5 | 17060.71 | 4.1 | 3.9 | 22.5694 | 26.0417 | 25 | 30
3-speed PSC motor_60_20kW_1 |  | CKT 1 | 20[6] | 10 | 34121.42 | 4.1 | 3.9 | 50.2639 | 56.9583 | 60 | 60
3-speed PSC motor_60_20kW_2 |  | CKT 2 | 20[6] | 10 | 34121.42 | 4.1 | 3.9 | 45.1389 | 52.0833 | 50 | 60
5-speed high eff. ECM motor_18_5kW_1 | 18 | CKT 1 | 5 | 5 | 17060.71 | 3.2 | 3 | 26.5694 | 29.7917 | 30 | 30
5-speed high eff. ECM motor_18_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 3.2 | 3 | 37.8542 | 42.8125 | 40 | 45
5-speed high eff. ECM motor_18_10kW_1 |  | CKT 1 | 10[4] | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_24_5kW_1 | 24 | CKT 1 | 5 | 5 | 17060.71 | 3.2 | 3 | 26.5694 | 29.7917 | 30 | 30
5-speed high eff. ECM motor_24_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 3.2 | 3 | 37.8542 | 42.8125 | 40 | 45
5-speed high eff. ECM motor_24_10kW_1 |  | CKT 1 | 10[4] | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_25_5kW_1 | 25 | CKT 1 | 5 | 5 | 17060.71 | 3.2 | 3 | 26.5694 | 29.7917 | 30 | 30
5-speed high eff. ECM motor_25_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 3.2 | 3 | 37.8542 | 42.8125 | 40 | 45
5-speed high eff. ECM motor_25_10kW_1 |  | CKT 1 | 10[4] | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_30_5kW_1 | 30 | CKT 1 | 5 | 5 | 17060.71 | 3.2 | 3 | 26.5694 | 29.7917 | 30 | 30
5-speed high eff. ECM motor_30_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 3.2 | 3 | 37.8542 | 42.8125 | 40 | 45
5-speed high eff. ECM motor_30_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_30_15kW_1 |  | CKT 1 | 15[5] | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_30_15kW_2 |  | CKT 2 | 15[5] | 5 | 17060.71 | 3.2 | 3 | 22.5694 | 26.0417 | 25 | 30
5-speed high eff. ECM motor_31_5kW_1 | 31 | CKT 1 | 5 | 5 | 17060.71 | 3.2 | 3 | 26.5694 | 29.7917 | 30 | 30
5-speed high eff. ECM motor_31_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 3.2 | 3 | 37.8542 | 42.8125 | 40 | 45
5-speed high eff. ECM motor_31_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_31_15kW_1 |  | CKT 1 | 15[5] | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_31_15kW_2 |  | CKT 2 | 15[5] | 5 | 17060.71 | 3.2 | 3 | 22.5694 | 26.0417 | 25 | 30
5-speed high eff. ECM motor_36_5kW_1 | 36 | CKT 1 | 5 | 5 | 17060.71 | 3.2 | 3 | 26.5694 | 29.7917 | 30 | 30
5-speed high eff. ECM motor_36_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 3.2 | 3 | 37.8542 | 42.8125 | 40 | 45
5-speed high eff. ECM motor_36_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_36_15kW_1 |  | CKT 1 | 15[5] | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_36_15kW_2 |  | CKT 2 | 15[5] | 5 | 17060.71 | 3.2 | 3 | 22.5694 | 26.0417 | 25 | 30
5-speed high eff. ECM motor_37_5kW_1 | 37 | CKT 1 | 5 | 5 | 17060.71 | 3.2 | 3 | 26.5694 | 29.7917 | 30 | 30
5-speed high eff. ECM motor_37_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 3.2 | 3 | 37.8542 | 42.8125 | 40 | 45
5-speed high eff. ECM motor_37_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_37_15kW_1 |  | CKT 1 | 15[5] | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_37_15kW_2 |  | CKT 2 | 15[5] | 5 | 17060.71 | 3.2 | 3 | 22.5694 | 26.0417 | 25 | 30
5-speed high eff. ECM motor_42_5kW_1 | 42 | CKT 1 | 5 | 5 | 17060.71 | 3.2 | 3 | 26.5694 | 29.7917 | 30 | 30
5-speed high eff. ECM motor_42_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 3.2 | 3 | 37.8542 | 42.8125 | 40 | 45
5-speed high eff. ECM motor_42_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_42_15kW_1 |  | CKT 1 | 15[5] | 10 | 34121.42 | 3.2 | 3 | 49.1389 | 55.8333 | 50 | 60
5-speed high eff. ECM motor_42_15kW_2 |  | CKT 2 | 15[5] | 5 | 17060.71 | 3.2 | 3 | 22.5694 | 26.0417 | 25 | 30
5-speed high eff. ECM motor_48_5kW_1 | 48 | CKT 1 | 5 | 5 | 17060.71 | 4.5 | 4.3 | 28.1944 | 31.4167 | 30 | 35
5-speed high eff. ECM motor_48_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591.065 | 4.5 | 4.3 | 39.4792 | 44.4375 | 40 | 45
5-speed high eff. ECM motor_48_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 4.5 | 4.3 | 50.7639 | 57.4583 | 60 | 60
5-speed high eff. ECM motor_48_15kW_1 |  | CKT 1 | 15 | 10 | 34121.42 | 4.5 | 4.3 | 50.7639 | 57.4583 | 60 | 60
5-speed high eff. ECM motor_48_15kW_2 |  | CKT 2 | 15 | 5 | 17060.71 | 4.5 | 4.3 | 22.5694 | 26.0417 | 25 | 30
5-speed high eff. ECM motor_48_20kW_1 |  | CKT 1 | 20[6] | 10 | 34121.42 | 4.5 | 4.3 | 50.7639 | 57.4583 | 60 | 60
5-speed high eff. ECM motor_48_20kW_2 |  | CKT 2 | 20[6] | 10 | 34121.42 | 4.5 | 4.3 | 45.1389 | 52.0833 | 50 | 60
5-speed high eff. ECM motor_60_7.5kw_1 | 60 | CKT 1 | 7.5 | 7.5 | 25591.065 | 4.9 | 4.6 | 39.9792 | 44.8125 | 40 | 45
5-speed high eff. ECM motor_60_10kW_1 |  | CKT 1 | 10 | 10 | 34121.42 | 4.9 | 4.6 | 51.2639 | 57.8333 | 60 | 60
5-speed high eff. ECM motor_60_15kW_1 |  | CKT 1 | 15 | 10 | 34121.42 | 4.9 | 4.6 | 51.2639 | 57.8333 | 60 | 60
5-speed high eff. ECM motor_60_15kW_2 |  | CKT 2 | 15 | 5 | 17060.71 | 4.9 | 4.6 | 22.5694 | 26.0417 | 25 | 30
5-speed high eff. ECM motor_60_20kW_1 |  | CKT 1 | 20[6] | 10 | 34121.42 | 4.9 | 4.6 | 51.2639 | 57.8333 | 60 | 60
5-speed high eff. ECM motor_60_20kW_2 |  | CKT 2 | 20[6] | 10 | 34121.42 | 4.9 | 4.6 | 45.1389 | 52.0833 | 50 | 60
[1] kW packages in bold italics require and include circuit breakers; circuit breakers are optional for others.
[2] For 208 volt use 0.751 correction factor for kW & BTUH.
[3] Breaker supplied with heat kit may need to be changed. Verify breaker sizing based on min, circuit ampacity.
[4] 10 kW electric heat must not be used in downflow configuration
[5] 15 kW electric heat must be operated at high speed setting in downflow configuration
[6] 20 kW electric heat must be operated at medium speed setting in downflow configuration

## Dim (hidden)
Unit size | A (in) | B (in) | C (in) | Depth (in) | Width (in) | Depth (in) | Width (in) | (-S Option)
18 | 36 | 22 | 15 | 17 | 13 | 20.35 | 12.2 | 6
24 | 36 | 22 | 15 | 17 | 13 | 20.35 | 12.2 | 6
25 | 41 | 22 | 18.5 | 17 | 16.5 | 20.35 | 16.2 | 4
30 | 41 | 22 | 18.5 | 17 | 16.5 | 20.35 | 16.2 | 4
36 | 41 | 22 | 18.5 | 17 | 16.5 | 20.35 | 16.2 | 4
31 | 48 | 26 | 21.88 | 21 | 20 | 24.6 | 20.08 | 2
37 | 48 | 26 | 21.88 | 21 | 20 | 24.6 | 20.08 | 2
42 | 48 | 26 | 21.88 | 21 | 20 | 24.6 | 20.08 | 2
48 | 48 | 26 | 21.88 | 21 | 20 | 24.6 | 20.08 | 2
60 | 48 | 26 | 21.88 | 21 | 20 | 24.6 | 20.08 | 2