## Front
SUBMITTAL DATA
mFurnaceTM AIR HANDLER
Job: |  |  |  | Engineer:
Location: |  |  |  | Architect:
Schedule No.: |  |  |  | Date:
System Designation: |  |  |  | For:
FEATURES
Product Warranty
Optional Accessories
Unit Size
|  | AMHE3D10B2N1 | AMHE4D00B2N1 | AMHE5D00B2N1 | AMHE5D00B2N1
Factory Installed Heat (kW) |  | 10kw | none | none | none
Blower Data: | Motor Type | 5-speed ECM motor | 5-speed ECM motor | 5-speed ECM motor | 5-speed ECM motor
| Motor H.P. | 1/2 | 3/4 | 3/4 | 3/4
| F.L.A. | 3.9 | 5.8 | 5.8 | 5.8
Nominal CFM |  | 900 - 1100 | 1200 - 1400 | 1200 - 1800 | 1200 - 1800
Max Unit Weight (lbs) |  | 85 | 85 | 100 | 100
Available Voltages |  | 208/240 V, 60 Hz, 1 ph. | 208/240 V, 60 Hz, 1 ph. | 208/240 V, 60 Hz, 1 ph. | 208/240 V, 60 Hz, 1 ph.
Maximum Elec. Heat available (kW) |  | 15kW | 20kW | 20kW | 20kW
Transformer Size and Type |  | 40 VA, Class 2 | 40 VA, Class 2 | 40 VA, Class 2 | 40 VA, Class 2
Product Nomenclature
2140 Lake Park Blvd., Richardson, TX 75080
www.adpnow.com
Standard footprint for installation in manufactured homes.
Compatible with 2-5 Ton AC or HP systems.
Factory configured for downflow, field convertible for up-flow.
Perfectly matches with ADP manufactured housing coils.
Meets UL 60335-2-40 product requirements.
Blower panel with handle and push-to-lock feature for easy access.
Cabinet and door lined with high quality 5/8" foil faced insulation for quiet operation.
Cabinet constructed of heavy-gauge, corrosion-resistant galvanized steel.
Slide-out blower assemblies for easy access to blower motor.
Multiple coil cabinet and filter grille options available.
Electric heat available factory or field installed for 208/240 V models.
5-year limited warranty (Terms & Conditions Apply).
Product improvement is a continuous process at Advanced Distributor Products. Therefore, product specifications are subject to change without notice and without obligation on our part. Please contact your ADP representative or distributor to verify details.
© 2025 by Advanced Distributor Products. All rights reserved.

## Back
SUBMITTAL DATA
mFurnaceTM AIR HANDLER
| Airflow (CFM) vs. External Static Pressure (inches W.C.) | [10 empty] | Electric Data
Unit Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size[2] (A)
AMHE3D10B2N1 | 1 | 414 | 344 | 268 | 202 | 202 | 201 | 201 | 201 | 202 | 202 |  |  |  | kW | BTUH
| 2 | 760 | 701 | 659 | 613 | 568 | 522 | 486 | 447 | 447 | 446 |  |  |  | 240 V[1] | 240 V[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| 3^ | 1063 | 956 | 916 | 873 | 840 | 803 | 767 | 735 | 720 | 672 | AMHE3D10B2N1 | CKT 1 | 10 | 10 | 34121 | 3.9 | 3.9 | 40 | 45.6 | 50 | 57 | 50 | 60
| 4# | 1157 | 1060 | 1005 | 963 | 926 | 900 | 867 | 840 | 807 | 805
| 5* | 1213 | 1142 | 1078 | 1035 | 997 | 961 | 936 | 905 | 881 | 848
[12 empty] | Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size[2] (A)
Unit Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 |  |  |  | kW | BTUH
AMHE4D00B2N1 | 1 | 486 | 408 | 333 | 253 | 216 | 216 | 216 | 216 | 216 | 216 |  |  |  | 240 V[1] | 240 V[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| 2 | 1046 | 1010 | 969 | 877 | 824 | 780 | 734 | 690 | 655 | 615 | AMHE4D00B2N1 | CKT 1 | 0 | 0 | 0 | 6 | 5.8 | 6 | 5.8 | 7.5 | 7.3 | 15 | 15
| 3^ | 1382 | 1347 | 1313 | 1286 | 1244 | 1194 | 1119 | 1068 | 1034 | 993
| 4# | 1426 | 1389 | 1353 | 1318 | 1289 | 1241 | 1179 | 1111 | 1068 | 1034
| 5* | 1501 | 1474 | 1443 | 1411 | 1377 | 1339 | 1304 | 1243 | 1178 | 1134 | Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size[2] (A)
[15 empty] | kW | BTUH
Unit Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 |  |  |  | 240 V[1] | 240 V[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
AMHE5D00B2N1 | 1 | 858 | 798 | 731 | 661 | 596 | 536 | 492 | 450 | 449 | 449 | AMHE5D00B2N1 | CKT 1 | 0 | 0 | 0 | 6 | 5.8 | 6 | 5.8 | 7.5 | 7.3 | 15 | 15
| 2 | 1053 | 1015 | 962 | 904 | 848 | 790 | 738 | 693 | 643 | 639
| 3 | 1202 | 1160 | 1116 | 1068 | 1013 | 965 | 911 | 861 | 818 | 810
| 4#,^ | 1343 | 1318 | 1281 | 1240 | 1196 | 1160 | 1106 | 1060 | 1014 | 1008 | Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | BTotal Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size[2] (A)
| 5* | 1826 | 1799 | 1790 | 1761 | 1722 | 1677 | 1640 | 1594 | 1544 | 1494 |  |  |  | kW | BTUH
[15 empty] | 240 V[1] | 240 V[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
Unit Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | AMHE5D00B2N1 | CKT 1 | 0 | 0 | 0 | 6 | 5.8 | 6 | 5.8 | 7.5 | 7.3 | 15 | 15
AMHE5D00B2N1 | 1 | 858 | 798 | 731 | 661 | 596 | 536 | 492 | 450 | 449 | 449
| 2 | 1053 | 1015 | 962 | 904 | 848 | 790 | 738 | 693 | 643 | 639
| 3 | 1202 | 1160 | 1116 | 1068 | 1013 | 965 | 911 | 861 | 818 | 810
| 4#,^ | 1343 | 1318 | 1281 | 1240 | 1196 | 1160 | 1106 | 1060 | 1014 | 1008
| 5* | 1826 | 1799 | 1790 | 1761 | 1722 | 1677 | 1640 | 1594 | 1544 | 1494
All data is given while air handler is operating with a dry coil and air filter installed.
Speeds marked bold with * are the factory speed settings for Cooling.
Speeds marked bold with # are the factory speed settings for Heating.
Speeds marked bold with ^ are minimum speed tap allowed for electric heating.
Different speeds can be set for cooling mode; see installation instructions for changing cooling speeds.
Speed tap 4 is the maximum allowed for electric heating and heat pump operation in AMHE5D models.
[1] For 208 volt use 0.751 correction factor for kW & BTUH.
[2] Verify breaker sizing based on minimum circuit ampacity.
* Circuit Breaker supplied with heat kit must be changed.

## Nomenclature (hidden)
AMH | E |  | 4 |  | D |  | 10 |  | B |  | 2 |  | N |  | 1
Series | Blower Motor |  | Unit Size |  | Configuration |  | Electric Heat |  | Line Voltage Connection |  | Voltage |  | Coil Cabinet |  | Revision | Revision
AMH | E: | 5-speed ECM motor | 2: | 2 Ton | D: | Downflow | 00: | none (sizes 2-5) | S: | Stripped Wires | 1: | 120 V, 60 Hz, 1 ph. | N: | Not Included
|  |  | 3: | 3 Ton |  |  | 05: | 5kW (sizes 2-5) | B: | Circuit Breaker | 2: | 208/240 V, 60 Hz, 1 ph.
|  |  | 4: | 4 Ton |  |  | 07: | 7.5kW (sizes 2-5)
|  |  | 5: | 5 Ton |  |  | 10: | 10kW (sizes 2-5)
[7 empty] | 12: | 12kW (sizes 3-5)
[7 empty] | 15: | 15kW (sizes 3-5)
[7 empty] | 20: | 20kW (sizes 4-5)

## Data (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Part Number | Series | Blower Motor | Airflow Config. | Slab No. | Metering Device | Unit Size | Line Voltage Connection | Electric Heat | Voltage | Revision | Refrigerant (R22 or R-410A) | Factory Installed metering device | Blower Data: Motor H.P. | Blower Data: F.L.A. @ 240 V | Nominal CFM | Max Unit Weight (lbs) | Available Voltages | Maximum Elec. Heat available (kW) | Transformer Size and Type | Refrigerant Conn. (IDS) Suction | Refrigerant Conn. (IDS) Liquid | Pallet Quantity (min order per model) | Coil Cabinet
AMHE2D00S1N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 2 | Stripped Wires | none | 120 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/3 | 3.9 | 600 - 800 | 85 | 120 V, 60 Hz, 1 ph. | 10kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE2D00S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 2 | Stripped Wires | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/3 | 2.6 | 600 - 800 | 85 | 208/240 V, 60 Hz, 1 ph. | 10kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE2D00B1N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 2 | Circuit Breaker | none | 120 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/3 | 3.9 | 600 - 800 | 85 | 120 V, 60 Hz, 1 ph. | 10kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE2D00B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 2 | Circuit Breaker | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/3 | 2.6 | 600 - 800 | 85 | 208/240 V, 60 Hz, 1 ph. | 10kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE2D05S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 2 | Stripped Wires | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/3 | 2.6 | 600 - 800 | 85 | 208/240 V, 60 Hz, 1 ph. | 10kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE2D05B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 2 | Circuit Breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/3 | 2.6 | 600 - 800 | 85 | 208/240 V, 60 Hz, 1 ph. | 10kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE2D07S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 2 | Stripped Wires | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/3 | 2.6 | 600 - 800 | 85 | 208/240 V, 60 Hz, 1 ph. | 10kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE2D07B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 2 | Circuit Breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/3 | 2.6 | 600 - 800 | 85 | 208/240 V, 60 Hz, 1 ph. | 10kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE2D10S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 2 | Stripped Wires | 10kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/3 | 2.6 | 600 - 800 | 85 | 208/240 V, 60 Hz, 1 ph. | 10kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE2D10B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 2 | Circuit Breaker | 10kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/3 | 2.6 | 600 - 800 | 85 | 208/240 V, 60 Hz, 1 ph. | 10kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D00S1N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Stripped Wires | none | 120 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 5.8 | 900 - 1100 | 85 | 120 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D00S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Stripped Wires | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D00B1N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Circuit Breaker | none | 120 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 5.8 | 900 - 1100 | 85 | 120 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D00B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Circuit Breaker | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D05S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Stripped Wires | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D05B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Circuit Breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D07S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Stripped Wires | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D07B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Circuit Breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D10S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Stripped Wires | 10kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D10B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Circuit Breaker | 10kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D12S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Stripped Wires | 12.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D12B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Circuit Breaker | 12.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D15S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Stripped Wires | 15kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE3D15B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 3 | Circuit Breaker | 15kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 1/2 | 3.9 | 900 - 1100 | 85 | 208/240 V, 60 Hz, 1 ph. | 15kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D00S1N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Stripped Wires | none | 120 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 8.7 | 1200 - 1400 | 85 | 120 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D00S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Stripped Wires | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D00B1N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Circuit Breaker | none | 120 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 8.7 | 1200 - 1400 | 85 | 120 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D00B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Circuit Breaker | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D05S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Stripped Wires | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D05B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Circuit Breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D07S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Stripped Wires | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D07B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Circuit Breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D10S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Stripped Wires | 10kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D10B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Circuit Breaker | 10kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D12S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Stripped Wires | 12.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D12B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Circuit Breaker | 12.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D15S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Stripped Wires | 15kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D15B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Circuit Breaker | 15kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D20S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Stripped Wires | 20kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE4D20B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 4 | Circuit Breaker | 20kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1400 | 85 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D00S1N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Stripped Wires | none | 120 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 8.7 | 1200 - 1800 | 100 | 120 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D00S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Stripped Wires | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D00B1N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Circuit Breaker | none | 120 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 8.7 | 1200 - 1800 | 100 | 120 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D00B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Circuit Breaker | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D05S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Stripped Wires | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D05B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Circuit Breaker | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D07S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Stripped Wires | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D07B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Circuit Breaker | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D10S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Stripped Wires | 10kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D10B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Circuit Breaker | 10kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D12S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Stripped Wires | 12.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D12B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Circuit Breaker | 12.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D15S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Stripped Wires | 15kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D15B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Circuit Breaker | 15kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D20S2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Stripped Wires | 20kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included
AMHE5D20B2N1 | AMH Series | 5-speed ECM motor | Downflow | N/A | N/A | 5 | Circuit Breaker | 20kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | 1 | N/A | N/A | 3/4 | 5.8 | 1200 - 1800 | 100 | 208/240 V, 60 Hz, 1 ph. | 20kW | 40 VA, Class 2 | N/A | N/A | 1 | Not Included

## Airflow (hidden)
ID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | Voltage/Motor
2_5-speed ECM motor_1 | AMHE2D | 1 | 368 | 317 | 244 | 196 | 197 | 196 | 196 | 197 | 196 | 196 |  | 208/240 V, 60 Hz, 1 ph. (PSC only) | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
2_5-speed ECM motor_2 |  | 2 | 522 | 470 | 433 | 379 | 339 | 339 | 340 | 260 | 261 | 260 |  | 120 V, 60 Hz, 1 ph. (PSC only) | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
2_5-speed ECM motor_3 |  | 3^ | 711 | 675 | 634 | 604 | 565 | 525 | 493 | 449 | 450 | 449 |  | 208/240 V, 60 Hz, 1 ph. (ECM only) | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
2_5-speed ECM motor_4 |  | 4# | 837 | 801 | 774 | 738 | 705 | 676 | 645 | 614 | 607 | 605 | All data is given while air handler is operating with a dry coil and air filter installed. | 120 V, 60 Hz, 1 ph. (ECM only) | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
2_5-speed ECM motor_5 |  | 5* | 921 | 886 | 862 | 827 | 794 | 770 | 739 | 713 | 709 | 654 | Speeds marked bold with * are the factory speed settings for Cooling.
3_5-speed ECM motor_1 | AMHE3D | 1 | 414 | 344 | 268 | 202 | 202 | 201 | 201 | 201 | 202 | 202 | Speeds marked bold with # are the factory speed settings for Heating.
3_5-speed ECM motor_2 |  | 2 | 760 | 701 | 659 | 613 | 568 | 522 | 486 | 447 | 447 | 446 | Speeds marked bold with ^ are minimum speed tap allowed for electric heating.
3_5-speed ECM motor_3 |  | 3^ | 1063 | 956 | 916 | 873 | 840 | 803 | 767 | 735 | 720 | 672 | Different speeds can be set for cooling mode; see installation instructions for changing cooling speeds.
3_5-speed ECM motor_4 |  | 4# | 1157 | 1060 | 1005 | 963 | 926 | 900 | 867 | 840 | 807 | 805 | Speed tap 4 is the maximum allowed for electric heating and heat pump operation in AMHE5D models.
3_5-speed ECM motor_5 |  | 5* | 1213 | 1142 | 1078 | 1035 | 997 | 961 | 936 | 905 | 881 | 848
4_5-speed ECM motor_1 | AMHE4D | 1 | 486 | 408 | 333 | 253 | 216 | 216 | 216 | 216 | 216 | 216
4_5-speed ECM motor_2 |  | 2 | 1046 | 1010 | 969 | 877 | 824 | 780 | 734 | 690 | 655 | 615
4_5-speed ECM motor_3 |  | 3^ | 1382 | 1347 | 1313 | 1286 | 1244 | 1194 | 1119 | 1068 | 1034 | 993
4_5-speed ECM motor_4 |  | 4# | 1426 | 1389 | 1353 | 1318 | 1289 | 1241 | 1179 | 1111 | 1068 | 1034
4_5-speed ECM motor_5 |  | 5* | 1501 | 1474 | 1443 | 1411 | 1377 | 1339 | 1304 | 1243 | 1178 | 1134
5_5-speed ECM motor_1 | AMHE5D | 1 | 858 | 798 | 731 | 661 | 596 | 536 | 492 | 450 | 449 | 449
5_5-speed ECM motor_2 |  | 2 | 1053 | 1015 | 962 | 904 | 848 | 790 | 738 | 693 | 643 | 639
5_5-speed ECM motor_3 |  | 3 | 1202 | 1160 | 1116 | 1068 | 1013 | 965 | 911 | 861 | 818 | 810
5_5-speed ECM motor_4 |  | 4#,^ | 1343 | 1318 | 1281 | 1240 | 1196 | 1160 | 1106 | 1060 | 1014 | 1008
5_5-speed ECM motor_5 |  | 5* | 1826 | 1799 | 1790 | 1761 | 1722 | 1677 | 1640 | 1594 | 1544 | 1494

## Electrial data (hidden)
No Electric Heat
| Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size (A)
|  |  |  | kW | BTUH
|  |  |  | 120 V | 120 V | 120 V |  | 120 V |  | 120 V |  | 120 V
120 V, 60 Hz, 1 ph. (ECM only)_2_none_1 | 2 | 1 | 0 | 0 | 0 | 3.9 |  | 3.9 |  | 4.9 |  | 15 |  | 2 | none | 1 | 120 V, 60 Hz, 1 ph. (ECM only)
120 V, 60 Hz, 1 ph. (ECM only)_3_none_1 | 3 | 1 | 0 | 0 | 0 | 5.8 |  | 5.8 |  | 7.3 |  | 15 |  | 3 | none | 1 | 120 V, 60 Hz, 1 ph. (ECM only)
120 V, 60 Hz, 1 ph. (ECM only)_4_none_1 | 4 | 1 | 0 | 0 | 0 | 8.7 |  | 8.7 |  | 10.9 |  | 15 |  | 4 | none | 1 | 120 V, 60 Hz, 1 ph. (ECM only)
120 V, 60 Hz, 1 ph. (ECM only)_5_none_1 | 5 | 1 | 0 | 0 | 0 | 8.7 |  | 8.7 |  | 10.9 |  | 15 |  | 5 | none | 1 | 120 V, 60 Hz, 1 ph. (ECM only)
Electric Data
| Unit Size | Circuit | Total Heat Capacity | Electric Heating capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size[3] (A)
|  |  |  | kW[1] | BTUH
|  |  |  | 240 V[2] | 240 V[2] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
208/240 V, 60 Hz, 1 ph. (ECM only)_2_none_1 | 2 | CKT 1 | 0 | 0 | 0 | 2.7 | 2.6 | 2.7 | 2.6 | 3.4 | 3.3 | 15 | 15 | 2 | none | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_2_5kw_1 |  | CKT 1 | 5 | 5 | 17061 | 2.7 | 2.6 | 20.8 | 23.4 | 25.9 | 29.3 | 30 | 30* | 2 | 5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_2_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591 | 2.7 | 2.6 | 29.8 | 33.9 | 37.2 | 42.3 | 40 | 45 | 2 | 7.5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_2_10kw_1 |  | CKT 1 | 10 | 10 | 34121 | 2.7 | 2.6 | 38.8 | 44.3 | 48.5 | 55.3 | 50 | 60 | 2 | 10kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_3_none_1 | 3 | CKT 1 | 0 | 0 | 0 | 3.9 | 3.9 | 3.9 | 3.9 | 4.9 | 4.9 | 15 | 15 | 3 | none | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_3_5kw_1 |  | CKT 1 | 5 | 5 | 17061 | 3.9 | 3.9 | 22 | 24.7 | 27.4 | 30.9 | 30 | 35 | 3 | 5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_3_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591 | 3.9 | 3.9 | 31 | 35.2 | 38.7 | 43.9 | 40 | 45 | 3 | 7.5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_3_10kw_1 |  | CKT 1 | 10 | 10 | 34121 | 3.9 | 3.9 | 40 | 45.6 | 50 | 57 | 50 | 60 | 3 | 10kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_3_12.5kw_1 |  | CKT 1 | 12.5 | 8.3 | 28321 | 3.9 | 3.9 | 33.9 | 38.5 | 42.3 | 48.1 | 45 | 50 | 3 | 12.5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_3_12.5kw_2 |  | CKT 2 | 12.5 | 4.2 | 14331 | 0 | 0 | 15.2 | 17.5 | 19 | 21.9 | 20 | 25 | 3 | 12.5kw | 2 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_3_15kw_1 |  | CKT 1 | 15 | 10 | 34121 | 3.9 | 3.9 | 40 | 45.6 | 50 | 57 | 50 | 60 | 3 | 15kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_3_15kw_2 |  | CKT 2 | 15 | 5 | 17061 | 0 | 0 | 18.1 | 20.8 | 22.6 | 26 | 25 | 30 | 3 | 15kw | 2 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_4_none_1 | 4 | CKT 1 | 0 | 0 | 0 | 6 | 5.8 | 6 | 5.8 | 7.5 | 7.3 | 15 | 15 | 4 | none | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_4_5kw_1 |  | CKT 1 | 5 | 5 | 17061 | 6 | 5.8 | 24.1 | 26.6 | 30.1 | 33.3 | 35 | 35 | 4 | 5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_4_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591 | 6 | 5.8 | 33.1 | 37.1 | 41.4 | 46.3 | 45 | 50* | 4 | 7.5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_4_10kw_1 |  | CKT 1 | 10 | 10 | 34121 | 6 | 5.8 | 42.1 | 47.5 | 52.6 | 59.3 | 60 | 60 | 4 | 10kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_4_12.5kw_1 |  | CKT 1 | 12.5 | 8.3 | 28321 | 6 | 5.8 | 36 | 40.4 | 45 | 50.5 | 45 | 60* | 4 | 12.5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_4_12.5kw_2 |  | CKT 2 | 12.5 | 4.2 | 14331 | 0 | 0 | 15.2 | 17.5 | 19 | 21.9 | 20 | 25 | 4 | 12.5kw | 2 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_4_15kw_1 |  | CKT 1 | 15 | 10 | 34121 | 6 | 5.8 | 42.1 | 47.5 | 52.6 | 59.3 | 60 | 60 | 4 | 15kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_4_15kw_2 |  | CKT 2 | 15 | 5 | 17061 | 0 | 0 | 18.1 | 20.8 | 22.6 | 26 | 25 | 30 | 4 | 15kw | 2 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_4_20kw_1 |  | CKT 1 | 20 | 10 | 34121 | 6 | 5.8 | 42.1 | 47.5 | 52.6 | 59.3 | 60 | 60 | 4 | 20kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_4_20kw_2 |  | CKT 2 | 20 | 10 | 34121 | 0 | 0 | 36.1 | 41.7 | 45.1 | 52.1 | 50 | 60 | 4 | 20kw | 2 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_5_none_1 | 5 | CKT 1 | 0 | 0 | 0 | 6 | 5.8 | 6 | 5.8 | 7.5 | 7.3 | 15 | 15 | 5 | none | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_5_5kw_1 |  | CKT 1 | 5 | 5 | 17061 | 6 | 5.8 | 24.1 | 26.6 | 30.1 | 33.3 | 35 | 35 | 5 | 5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_5_7.5kw_1 |  | CKT 1 | 7.5 | 7.5 | 25591 | 6 | 5.8 | 33.1 | 37.1 | 41.4 | 46.3 | 45 | 50* | 5 | 7.5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_5_10kw_1 |  | CKT 1 | 10 | 10 | 34121 | 6 | 5.8 | 42.1 | 47.5 | 52.6 | 59.3 | 60 | 60 | 5 | 10kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_5_12.5kw_1 |  | CKT 1 | 12.5 | 8.3 | 28321 | 6 | 5.8 | 36 | 40.4 | 45 | 50.5 | 45 | 60* | 5 | 12.5kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_5_12.5kw_2 |  | CKT 2 | 12.5 | 4.2 | 14331 | 0 | 0 | 15.2 | 17.5 | 19 | 21.9 | 20 | 25 | 5 | 12.5kw | 2 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_5_15kw_1 |  | CKT 1 | 15 | 10 | 34121 | 6 | 5.8 | 42.1 | 47.5 | 52.6 | 59.3 | 60 | 60 | 5 | 15kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_5_15kw_2 |  | CKT 2 | 15 | 5 | 17061 | 0 | 0 | 18.1 | 20.8 | 22.6 | 26 | 25 | 30 | 5 | 15kw | 2 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_5_20kw_1 |  | CKT 1 | 20 | 10 | 34121 | 6 | 5.8 | 42.1 | 47.5 | 52.6 | 59.3 | 60 | 60 | 5 | 20kw | 1 | 208/240 V, 60 Hz, 1 ph. (ECM only)
208/240 V, 60 Hz, 1 ph. (ECM only)_5_20kw_2 |  | CKT 2 | 20 | 10 | 34121 | 0 | 0 | 36.1 | 41.7 | 45.1 | 52.1 | 50 | 60 | 5 | 20kw | 2 | 208/240 V, 60 Hz, 1 ph. (ECM only)
[1] For 208 volt use 0.751 correction factor for kW & BTUH.
[2] Verify breaker sizing based on minimum circuit ampacity.
* Circuit Breaker supplied with heat kit must be changed.